## #1 Instructions
Tank and Dike Work Book
Instructions and Notes
1 | Purpose: This Excel Work Book was created to assist the Plant Layout Designer with a task that can be complicated, filled with potential error and take a lot of time. The goal is to reduce costs by reducing time and improving quality.
2 | Application: This Work Book can be used for single tank within a single containment area or can be used for multiple tanks within a single containment area.
3 | Contents: There are five (5) sheets included. Sheet "1 (this sheet) is the instructions and Notes. Sheet #2 is a list of some of the most common API Storage Tank sizes. Space is included so the user can record other sizes consistent with project specific requirements. Sheet #3 is the work sheet for the Single Tank application. Sheet #4 is the work Sheet for the multiple tank application. Sheet #5 is a two page work sheet: Page 1 is for the Dike Detail and page 2 is for the Tank Pad Detail.
4 | Tank Data: A) Collect a list of Tanks for the Project. This list must include the sizes (in Barrels), the Tank Types and the Commodities. B) Determine if there is a Local or Client imposed Code that defines Grouping or separation of Tank types or Commodities. If there are Tanks on the project list that are not included on Sheet #2 then add them in the "Yellow" spaces provided and in this case only hit "Save".
5 | Civil/Structural Data: Meet with the appropriate Civil/Structural Group and have them define preliminary guidelines for A) the Angle of Repose of the material to be used for the Dikes (Berms, Bungs, etc.), the recommended maximum height of the Dikes B) The proposed approach to Tank Pad profiles (Height and configuration) and C) any required "freeboard" associated with rainwater and/or firewater.
6 | The Task: Add the Dike Height and Angle of Repose ratio into Page 1 of Sheet #5. Add the Tank Pad height Data to Page 2 of Sheet #5.
7 | For Single Tank Installation: Use Sheet #3. Enter all the data required (and Optional) Data in the "Yellow" user entry boxes. The Form and the built-in formulas will do the work for you.
8 | For Multiple Tank Installation: Use Sheet #4. Enter all the data required (and Optional) Data in the "Yellow" user entry boxes. The Form and the built-in formulas will do most of the work for you. With this grouping you must select and enter a choice for the "Width" of the Containment Area. This is a "Trial and Error" method until you get the shape that fits the project needs.
9 | Quitting and Closing: It is recommended that before closing the program that Copies of all Sheets be printed out for all Tank configurations completed. When closing the program do not save the data. This will allow you to start with a clean Work Book for the next Tank configuration.
Note: | Each Sheet of this Work Book is Password protected. In order to make a change to a "cell" that is not "Yellow" the Sheet must be "unprotected" using the password. This Password will be furnished on request.

## #2 Tank Capacities
User add data as required in yellow boxes (#1, #2 & #3) if provided data is not applicable
The information shown here is based on API Standard Storage Tanks commonly used in Tank Farm installations. | Capacity | [5 empty] | Diameter |  | Height
| Barrels | Gallons (US) | Gallons (UK) | Cubic Feet | Cubic Yards | Cubic Meters | Feet | Meters | Feet | Meters
| 2500 | 105000 | 87430.749 | 14036.463 | 519.8689 | 397.5208 | 21.25 | 6.477 | 40 | 12.192
| 5000 | 210000 | 174861.498 | 28072.926 | 1039.7377 | 795.0415 | 30 | 9.144 | 40 | 12.192
| 7500 | 315000 | 262292.247 | 42109.389 | 1559.6066 | 1192.5623 | 37 | 11.2776 | 40 | 12.192
| 10000 | 420000 | 349722.996 | 56145.852 | 2079.4754 | 1590.083 | 42.5 | 12.954 | 40 | 12.192
| 12000 | 504000 | 419667.5952 | 67375.0224 | 2495.3705 | 1908.0996 | 46.5 | 14.1732 | 40 | 12.192
| 15000 | 630000 | 524584.494 | 84218.778 | 3119.2132 | 2385.1246 | 52 | 15.8496 | 40 | 12.192
| 20000 | 840000 | 699445.992 | 112291.704 | 4158.9509 | 3180.1661 | 60 | 18.288 | 40 | 12.192
| 25000 | 1050000 | 874307.49 | 140364.63 | 5198.6886 | 3975.2076 | 67 | 20.4216 | 40 | 12.192
| 30000 | 1260000 | 1049168.988 | 168437.556 | 6238.4263 | 4770.2491 | 73.5 | 22.4028 | 40 | 12.192
| 35000 | 1470000 | 1224030.486 | 196510.482 | 7278.164 | 5565.2906 | 79.5 | 24.2316 | 40 | 12.192
| 40000 | 1680000 | 1398891.984 | 224583.408 | 8317.9018 | 6360.3322 | 85 | 25.908 | 40 | 12.192
| 50000 | 2100000 | 1748614.98 | 280729.26 | 10397.3772 | 7950.4152 | 86 | 26.2128 | 40 | 12.192
| 55000 | 2310000 | 1923476.478 | 308802.186 | 11437.1149 | 8745.4567 | 100 | 30.48 | 40 | 12.192
| 60000 | 2520000 | 2098337.976 | 336875.112 | 12476.8526 | 9540.4982 | 105 | 32.004 | 40 | 12.192
| 60000 | 2520000 | 2098337.976 | 336875.112 | 12476.8526 | 9540.4982 | 95 | 28.956 | 48 | 14.6304
| 65000 | 2730000 | 2273199.474 | 364948.038 | 13516.5904 | 10335.5398 | 108.5 | 33.0708 | 40 | 12.192
| 70000 | 2940000 | 2448060.972 | 393020.964 | 14556.3281 | 11130.5813 | 113 | 34.4424 | 40 | 12.192
| 70000 | 2940000 | 2448060.972 | 393020.964 | 14556.3281 | 11130.5813 | 103 | 31.3944 | 48 | 14.6304
| 80000 | 3360000 | 2797783.968 | 449166.816 | 16635.8035 | 12720.6643 | 121 | 36.8808 | 40 | 12.192
| 80000 | 3360000 | 2797783.968 | 449166.816 | 16635.8035 | 12720.6643 | 110 | 33.528 | 48 | 14.6304
| 90000 | 3780000 | 3147506.964 | 505312.668 | 18715.279 | 14310.7474 | 116.5 | 35.5092 | 48 | 14.6304
| 95000 | 3990000 | 3322368.462 | 533385.594 | 19755.0167 | 15105.7889 | 120 | 36.576 | 48 | 14.6304
User add tank capacity as required |  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
|  | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0
| #1 | [5 empty] | #2 |  | #3

## #3 Single Tank
Tank & Dike Calculation Sheet #1
|  |  |  | Single Tank in Single Dike Area |  |  |  | The user only fills in data in the appropriate "Yellow" boxes. No. 1, 2, 3, 4, 5 (optional), 6, 7, 8 are required. The minimum length #9 is calculated.
[5 empty] | #2 Tank Number |  | #3 By |  | #4 Date
A | #1 Project -
| Capacity | [5 empty] | #7 Diameter |  | #5 Height (Information only)
| Barrels | Gallons (US) | Gallons (UK) | Cubic Feet | Cubic Yards | Cubic Meters | Feet | Meters | Feet | Meters
B |  | 0 | 0 | 0 | 0 | 0
| #6 | Volume (110%) |  | 0 |  | 0
| See Note @ #9 |  | Minimum Toe of Dike to Crown of Dike if Dike area is square (North/South direction) |  |  | #DIV/0! | Feet |  |  | See Note @ #9
[6 empty] | #DIV/0! | Meters
(Same in East/West direction)
|  |  | Tank Diameter - |  | 0 |  | Feet
`
|  |  | Tank Diameter - |  | 0 |  | Meters |  |  | From Sheet #5 for Dike Details
|  |  | 15 ft or 5m Min. |  |  |  | 15 ft or 5m Min. |  | #8 | Dike Height
[10 empty] | 0 | Feet
[10 empty] | 0 | Meters
|  | Apron width | From Sheet #5 Pad Details |  | Effective Tank Pad Diameter |  |  | Pad Height | From Sheet #5 Pad Details
| Feet | 0 |  |  | 0 | Feet | Feet | 0
| Meters | 0 |  |  | 0 | Meters | Meters | 0
[5 empty] | Tank Pad |  | Dike Containment Area
[5 empty] | Pad Volume |  | Total Volume Required (*) |  | Minimum Dike surface area | Min. Req'd Length/Width | #9
|  | Pad slope width | From Sheet #5 Pad Details |  | 0 | Cubic Feet | 0 |  | #DIV/0! | #DIV/0! | Feet
| Feet | 0 |  |  | 0 | Cubic Meters | 0 |  | #DIV/0! | #DIV/0! | Meters
| Meters | 0 |  |  |  |  | (*) Total Volume required includes Tank contents plus Pad displacement volume. |  |  | Note: For Total Outside Toe to Outside Toe Dimension add dim "Y" & "Z" from Sheet #5

## #4 Multi Tank
Tank & Dike Calculation Sheet
The user only fills in data in the approprate "Yellow" boxes. No. 1, 2, 3, 4, 5 (optional), 6, 7, 8 are required. The length is calculated in #10. |  |  |  |  | Multiple Tanks in Single Dike Area
[6 empty] | #2 Tank Numbers |  | #3 By |  | #4 Date
| A | #1 Project -
Largest Tk. |  | Capacity | [5 empty] | #7 Diameter |  | #5 Height(Optional)
|  | #6 Barrels | Gallons (US) | Gallons (UK) | Cubic Feet | Cubic Yards | Cubic Meters | Feet | Meters | Feet | Meters
| B1 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | Displacement Volume of smaller Multi-Tank
|  |  | Volume (110%) |  | 0 |  | 0 | [7 empty] | Cubic Feet | [5 empty] | Cubic Meters
[14 empty] | Tank # | Diameter | Radius | Area (sq. Ft.) | Pad Height | Dike Height | Volume | Diameter | Radius | Area | Pad Height | Dike Height | Volume
Smaller Tks. | C1 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C2 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C3 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C4 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| C5 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Volume Largest Tank = |  |  | 0 |  | 0 | [11 empty] | Total | 0 | Cu. Ft |  |  |  | Total | 0 | Cu. Meters
|  | Displacement Volume of Smaller Tanks = |  |  | 0 |  | 0
|  | Displacement Volume of Pads = |  |  | 0 |  | 0 |  |  |  |  | Note: For Total Outside Toe to Outside Toe Dimension add dim "Y" & "Z" from Sheet #5
|  | Total Volume of Containment area = |  |  | 0 |  | 0
[5 empty] | Cu. Ft | #9 | Cu. Meters | #10
|  |  | Minimum Width must include Largest Tank Pad Dia + Maintence between the Dike & Pad |  |  | Selected Width |  | Minimum Length
[7 empty] | Feet | #DIV/0! |  | Feet
[6 empty] | 0 | Meters | #DIV/0! |  | Meters
|  |  | Tank Diameter - |  | 0 |  | Feet
|  |  | Tank Diameter - |  | 0 |  | Meters
See Sht. #5 for Dike Height
Maint. Clearance
[12 empty] | Dike Height | #8
|  |  | 15 Feet |  | Largest Tank | [6 empty] | 0 | Feet
|  |  | 5 Meters |  |  |  |  | Smaller Tank (s) |  |  |  | 0 | Meters
Pad Height
[5 empty] | Effective Tank Pad Diameter |  |  | See Sheet #5
See Sheet #5

## #5 Dike Pad Detail
Page 1
| Dike Width Calculation Detail | [6 empty] | The user must fill in appropriate data in the "Yellow" boxes at No. 1, 2 , 3 and 4
|  | #1 | Crown Walkway |  |  |  |  | This dimension "X" is determined by the "Angle of Repose" for the material used for the Dike. Concrete wall would be 1:0 ratio but desert sand might be 1:3 ratio. You must talk to Civil to get guidance. |  |  | #2
|  | Actual = | 0 | decimal of feet | [6 empty] | Required Angle Ratio
| Recommended = |  | 3 Feet Min. |  | "X" | [5 empty] | 1 To | 1
| Recommended = |  | 1 Meter Min.
|  | Actual = |  | decimal of meter
#3
[8 empty] | "Freeboard" This is the safety space for Rain or Fire Water volume |  |  | 0 | Feet
[11 empty] | 0 | Meters
[8 empty] | Max selected Dike height |  | 0 | Feet
[10 empty] | 0 | Meters
|  | Dike Profile | [8 empty] | #4
[8 empty] | This is the minimum height required for the 110% full tank spill volume |  |  | 0 | Feet
Meters
`
Angle of Repose Ratio Example- 1:1, 1:1.5, 1:2
Minimum Toe to Toe Dike width
|  |  |  | Dim "Y" |  |  |  | Item | Imperial | Metric
[8 empty] | "X" | 0 | 0
[8 empty] | Walkway | 0 | 0 | 0 | 0
|  |  |  | Dim. "Z" |  |  |  | Total = | 0 | 0 | 0 | 0
[9 empty] | Dimension "Z" |  | Dimension "Y"
Page 2
Pad Volume Calculation Detail |  |  |  |  | Tank Diameter |  |  | The user must fill in appropriate data in the "Yellow" boxes at No. 5, 6 and 7
Tank Wall
|  |  | Pad Slope | Pad Apron
Tank Bottom
Tank Pad
Effective Tank Pad diameter equals the Tank Diameter + the Pad Apron for both sides & one Pad Slope
|  | Tank Diameter | Pad
|  |  | #5 Apron | #6 Slope | Diameter | Radius | Radius Sq. | Area | #7 Height | Volume (Single Tank)
If Single Tank | B (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | Cubic Feet
| B (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | Cu. Meters
Largest If Multiple Tank | B1 (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| B1 (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
Smaller multiple Tks. | C1 (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C1 (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C2 (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C2 (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C3 (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C3(m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C4 (ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C4 (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C5 (Ft) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
| C5 (m) | 0 |  |  | 0 | 0 | 0 | 0 |  | 0
[7 empty] | Pad Volume for multiple Tanks |  |  | 0 | Cubic Feet
[10 empty] | 0 | Cu. Meters