## Index
Flange comparison Guide
Select Size Below for comparison
½" | DN15 |  | 3" | DN80 | 14" | DN350
¾" | DN20 |  | 4" | DN100 | 15" | DN375
1" | DN25 |  | 5" | DN125 | 16" | DN400
1¼" | DN32 |  | 6" | DN150 | 18" | DN450
1½" | DN40 |  | 8" | DN200 | 20" | DN500
2" | DN50 |  | 10" | DN250 | 24" | DN600
2½" | DN65 |  | 12" | DN300
What is DN?
DN stands for 'Diameter Nominale'.
Put simply, it is a rough translation of mm from imperial sizes, assuming that an inch is 25mm.
We refer to a 12" flange as DN300, when in fact it is 304mm.
What is the PCD?
The PCD of a flange is one of the critical dimensions.
PCD (Pitch Circle Diameter) is the diameter of a circle that goes through each of the bolt holes.
There are several standards for flanges, and we deal with four of them;
British Standard - BS10 | Table D |  | Table E is the most popular for applications with water. All dimensions are specified in inches.
Table E
Table F
Table G
Table H
Table J
Table K
Australian Standard - AS2129 | Table C |  | These flanges are equivalent to the BS10 flanges, except that all dimensions are specified in mm. In some sizes, bolt holes are slightly larger to give better clearance.
Table D
Table E
Table F
Table G
Table H
Table J
American National Standards Institute (ANSI) | ANSI 125 |  | Higher numbers denote higher pressures. Sometimes people use the word 'Class' instead of ANSI. e.g. an ANSI 150 flange might be called a 'Class 150'. All dimensions are specified in inches.
ANSI 150
ANSI 300
ANSI 600
ANSI 900
ANSI 1500
British Standard - BS4504 | BS4504-6 | PN6 | Engineers use the prefix PN (Pressure Nominale). e.g. a BA4504-16 flange will commonly be referred to as a PN16. Generally, a PN16 flange is designed to withstand pressures up to 16 bar. All dimensions are specified in mm.
| BS4504-10 | PN10
| BS4504-16 | PN16
| BS4504-25 | PN25
| BS4504-40 | PN40
| BS4504-64 | PN64
| BS4504-100 | PN100

## DN15
Return To Index Page
Size = DN15
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 3 1/2" / 89mm | 2 3/8" / 60mm | 4 | 1/2" | 5/8" / 16mm |  | 5/16" / 8mm | 5/16" / 8mm
ANSI 600 | 3 3/4" / 95mm | 2 5/8" / 67mm | 4 | 1/2" | 5/8" / 16mm |  |  | 9/16" / 14mm
ANSI 900 | 4 3/4" / 121mm | 3 1/4" / 83mm | 4 | 3/4" | 7/8" / 22mm |  |  | 7/8" / 22mm
ANSI 1500 | 4 3/4" / 121mm | 3 1/4" / 83mm | 4 | 3/4" | 7/8" / 22mm |  |  | 7/8" / 22mm
AS2129 Table C | 95mm | 67mm | 4 | 13mm | 14mm | 13mm | 13mm | 10mm
AS2129 Table D | 95mm | 67mm | 4 | 13mm | 14mm | 13mm | 6mm | 10mm
AS2129 Table E | 95mm | 67mm | 4 | 13mm | 14mm | 13mm | 6mm | 10mm
AS2129 Table F | 95mm | 67mm | 4 | 13mm | 14mm | 13mm | 8mm | 10mm
AS2129 Table H | 14mm | 83mm | 4 | 16mm | 17mm | 16mm | 10mm | 13mm
AS2129 Table J | 114mm | 83mm | 4 | 16mm | 17mm |  | 16mm | 16mm
BS10 Table D | 3 3/4" / 95mm | 2 5/8" / 67mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 1/4" / 6mm | 3/8" / 10mm
BS10 Table E | 3 3/4" / 95mm | 2 5/8" / 67mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 1/4" / 6mm | 3/8" / 10mm
BS10 Table F | 3 3/4" / 95mm | 2 5/8" / 67mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 5/16" / 8mm | 3/8" / 10mm
BS10 Table H | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm | 5/8" / 16mm | 3/8" / 10mm | 1/2" / 13mm
BS10 Table J | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm |  | 5/8" / 16mm | 5/8" / 16mm
BS10 Table K | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm |  | 3/4" / 19mm | 3/4" / 19mm
BS4504-6 | 80mm | 55mm | 4 | M10 | 11mm | 12mm
BS4504-10 | 95mm | 65mm | 4 | M12 | 14mm | 14mm
BS4504-16 | 95mm | 65mm | 4 | M12 | 14mm | 14mm
BS4504-25 | 95mm | 65mm | 4 | M12 | 14mm | 16mm | 8mm | 16mm
BS4504-40 | 95mm | 65mm | 4 | M12 | 14mm |  | 9mm | 16mm
BS4504-64 | 105mm | 75mm | 4 | M12 | 14mm |  |  | 20mm
BS4504-100 | 105mm | 75mm | 4 | M12 | 14mm |  |  | 20mm

## DN20
Return To Index Page
Size = DN20
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 3 7/8" / 98mm | 2 3/4" / 70mm | 4 | 1/2" | 5/8" / 16mm |  | 11/32" / 9mm | 9/16" / 14mm
ANSI 300 | 4 5/8" / 117mm | 3 1/4" / 83mm | 4 | 5/8" | 3/4" / 19mm |  | 17/32" / 13mm | 5/8" / 16mm
ANSI 600 | 4 5/8" / 117mm | 3 1/4" / 83mm | 4 | 5/8" | 3/4" / 19mm |  |  | 5/8" / 16mm
ANSI 900 | 5 1/8" / 130mm | 3 1/2" / 89mm | 4 | 3/4" | 7/8" / 22mm |  |  | 1" / 25mm
ANSI 1500 | 5 1/8" / 130mm | 3 1/2" / 89mm | 4 | 3/4" | 7/8" / 22mm |  |  | 1" / 25mm
AS2129 Table C | 100mm | 73mm | 4 | 13mm | 14mm | 13mm | 13mm | 10mm
AS2129 Table D | 100mm | 73mm | 4 | 13mm | 14mm | 13mm | 6mm | 10mm
AS2129 Table E | 100mm | 73mm | 4 | 13mm | 14mm | 13mm | 6mm | 10mm
AS2129 Table F | 100mm | 73mm | 4 | 13mm | 14mm | 13mm | 8mm | 10mm
AS2129 Table H | 115mm | 83mm | 4 | 16mm | 18mm | 16mm | 10mm | 13mm
AS2129 Table J | 115mm | 83mm | 4 | 16mm | 18mm |  | 16mm | 16mm
BS10 Table D | 4" / 102mm | 2 7/8" / 73mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 1/4" / 6mm | 3/8" / 10mm
BS10 Table E | 4" / 102mm | 2 7/8" / 73mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 1/4" / 6mm | 3/8" / 10mm
BS10 Table F | 4" / 102mm | 2 7/8" / 73mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 5/16" / 8mm | 3/8" / 10mm
BS10 Table H | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm | 5/8" / 16mm | 3/8" / 10mm | 1/2" / 13mm
BS10 Table J | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm |  | 5/8" / 16mm | 5/8" / 16mm
BS10 Table K | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 5/8" | 11/16" / 17mm |  | 3/4" / 19mm | 3/4" / 19mm
BS4504-6 | 90mm | 65mm | 4 | M10 | 11mm | 14mm
BS4504-10 | 105mm | 75mm | 4 | M12 | 14mm | 16mm
BS4504-16 | 105mm | 75mm | 4 | M12 | 14mm | 16mm | 6mm | 18mm
BS4504-25 | 105mm | 75mm | 4 | M12 | 14mm | 18mm | 8mm | 18mm
BS4504-40 | 105mm | 75mm | 4 | M12 | 14mm |  | 9mm | 18mm
BS4504-64 | 130mm | 90mm | 4 | M16 | 18mm |  |  | 22mm
BS4504-100 | 130mm | 90mm | 4 | M16 | 18mm |  |  | 22mm

## DN25
Return To Index Page
Size = DN25
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 4 1/4" / 108mm | 3 1/8" / 79mm | 4 | 1/2" | 5/8" / 16mm | 7/16" / 11mm | 3/8" / 10mm | 7/16" / 11mm
ANSI 300 | 4 7/8" / 124mm | 3 1/2" / 89mm | 4 | 5/8" | 3/4" / 19mm |  | 19/32" / 15mm | 11/16" / 17mm
ANSI 600 | 4 7/8" / 124mm | 3 1/2" / 89mm | 4 | 5/8" | 3/4" / 19mm |  |  | 11/16" / 17mm
ANSI 900 | 5 7/8" / 149mm | 4" / 102mm | 4 | 7/8" | 1" / 25mm |  |  | 1 1/8" / 29mm
ANSI 1500 | 5 7/8" / 149mm | 4" / 102mm | 4 | 7/8" | 1" / 25mm |  |  | 1 1/8" / 29mm
AS2129 Table C | 115mm | 83mm | 4 | 16mm | 14mm | 13mm | 13mm | 10mm
AS2129 Table D | 115mm | 83mm | 4 | 13mm | 14mm | 13mm | 8mm | 10mm
AS2129 Table E | 115mm | 83mm | 4 | 13mm | 14mm | 13mm | 8mm | 10mm
AS2129 Table F | 120mm | 87mm | 4 | 16mm | 18mm | 13mm | 10mm | 10mm
AS2129 Table H | 120mm | 87mm | 4 | 16mm | 18mm | 19mm | 11mm | 14mm
AS2129 Table J | 120mm | 87mm | 4 | 16mm | 18mm |  | 19mm | 19mm
BS10 Table D | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 5/16" / 8mm | 3/8" / 10mm
BS10 Table E | 4 1/2" / 114mm | 3 1/4" / 83mm | 4 | 1/2" | 9/16" / 14mm | 1/2" / 13mm | 5/16" / 8mm | 3/8" / 10mm
BS10 Table F | 4 3/4" / 121mm | 3 7/16" / 87mm | 4 | 5/8" | 9/16" / 14mm | 1/2" / 13mm | 3/8" / 10mm | 3/8" / 10mm
BS10 Table H | 4 3/4" / 121mm | 3 7/16" / 87mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 7/16" / 11mm | 9/16" / 14mm
BS10 Table J | 4 3/4" / 121mm | 3 7/16" / 87mm | 4 | 5/8" | 11/16" / 17mm |  | 3/4" / 19mm | 3/4" / 19mm
BS10 Table K | 5" / 127mm | 3 3/4" / 95mm | 4 | 5/8" | 11/16" / 17mm |  | 7/8" / 22mm | 7/8" / 22mm
BS4504-6 | 100mm | 75mm | 4 | M10 | 11mm | 14mm
BS4504-10 | 115mm | 85mm | 4 | M12 | 14mm | 16mm
BS4504-16 | 115mm | 85mm | 4 | M12 | 14mm | 16mm | 8mm | 18mm
BS4504-25 | 115mm | 85mm | 4 | M12 | 14mm | 18mm | 9mm | 18mm
BS4504-40 | 115mm | 85mm | 4 | M12 | 14mm |  | 11mm | 18mm
BS4504-64 | 140mm | 100mm | 4 | M16 | 18mm |  |  | 24mm
BS4504-100 | 140mm | 100mm | 4 | M16 | 18mm |  |  | 24mm

## DN32
Return To Index Page
Size = DN32
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 4 5/8" / 117mm | 3 1/2" / 89mm | 4 | 1/2" | 5/8" / 16mm | 1/2" / 13mm | 13/32" / 10mm | 1/2" / 13mm
ANSI 300 | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 3/4" / 19mm |  | 5/8" / 16mm | 3/4" / 19mm
ANSI 600 | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 3/4" / 19mm |  |  | 13/16" / 21mm
ANSI 900 | 6 1/4" / 159mm | 4 3/8" / 111mm | 4 | 7/8" | 1" / 25mm |  |  | 1 1/8" / 29mm
ANSI 1500 | 6 1/4" / 159mm | 4 3/8" / 111mm | 4 | 7/8" | 1" / 25mm |  |  | 1 1/8" / 29mm
AS2129 Table C | 120mm | 87mm | 4 | 13mm | 14mm | 16mm | 16mm | 13mm
AS2129 Table D | 120mm | 87mm | 4 | 13mm | 14mm | 16mm | 8mm | 13mm
AS2129 Table E | 120mm | 87mm | 4 | 13mm | 14mm | 16mm | 8mm | 13mm
AS2129 Table F | 135mm | 98mm | 4 | 16mm | 18mm | 16mm | 10mm | 13mm
AS2129 Table H | 135mm | 98mm | 4 | 16mm | 18mm | 22mm | 11mm | 17mm
AS2129 Table J | 135mm | 98mm | 4 | 16mm | 18mm |  | 19mm | 19mm
BS10 Table D | 4 3/4" / 121mm | 3 7/16" / 87mm | 4 | 1/2" | 9/16" / 14mm | 5/8" / 16mm | 5/16" / 8mm | 1/2" / 13mm
BS10 Table E | 4 3/4" / 121mm | 3 7/16" / 87mm | 4 | 1/2" | 9/16" / 14mm | 5/8" / 16mm | 5/16" / 8mm | 1/2" / 13mm
BS10 Table F | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 11/16" / 17mm | 5/8" / 16mm | 3/8" / 10mm | 1/2" / 13mm
BS10 Table H | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 7/16" / 11mm | 11/16" / 17mm
BS10 Table J | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 11/16" / 17mm |  | 3/4" / 19mm | 3/4" / 19mm
BS10 Table K | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 5/8" | 11/16" / 17mm |  | 7/8" / 22mm | 7/8" / 22mm
BS4504-6 | 120mm | 90mm | 4 | M12 | 14mm | 16mm
BS4504-10 | 140mm | 100mm | 4 | M16 | 18mm | 18mm
BS4504-16 | 140mm | 100mm | 4 | M16 | 18mm | 18mm | 8mm | 18mm
BS4504-25 | 140mm | 100mm | 4 | M16 | 18mm | 20mm | 9mm | 18mm
BS4504-40 | 140mm | 100mm | 4 | M16 | 18mm |  | 11mm | 18mm
BS4504-64 | 155mm | 110mm | 4 | M20 | 22mm |  |  | 26mm
BS4504-100 | 155mm | 110mm | 4 | M20 | 22mm |  |  | 26mm

## DN40
Return To Index Page
Size = DN40
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 5" / 127mm | 3 7/8" / 98mm | 4 | 1/2" | 5/8" / 16mm | 9/16" / 14mm | 7/16" / 11mm | 9/16" / 14mm
ANSI 300 | 6 1/8" / 156mm | 4 1/2" / 114mm | 4 | 3/4" | 7/8" / 22mm |  | 11/16" / 17mm | 13/16" / 21mm
ANSI 600 | 6 1/8" / 156mm | 4 1/2" / 114mm | 4 | 3/4" | 7/8" / 22mm |  |  | 7/8" / 22mm
ANSI 900 | 7" / 178mm | 4 7/8" / 124mm | 4 | 1" | 1 1/8" / 29mm |  |  | 1 1/4" / 32mm
ANSI 1500 | 7" / 178mm | 4 7/8" / 124mm | 4 | 1" | 1 1/8" / 29mm |  |  | 1 1/4" / 32mm
AS2129 Table C | 135mm | 98mm | 4 | 13mm | 14mm | 16mm | 16mm | 13mm
AS2129 Table D | 135mm | 98mm | 4 | 13mm | 14mm | 16mm | 10mm | 13mm
AS2129 Table E | 135mm | 98mm | 4 | 13mm | 14mm | 16mm | 10mm | 13mm
AS2129 Table F | 140mm | 105mm | 4 | 16mm | 18mm | 16mm | 11mm | 13mm
AS2129 Table H | 140mm | 105mm | 4 | 16mm | 18mm | 22mm | 13mm | 17mm
AS2129 Table J | 140mm | 105mm | 4 | 16mm | 18mm |  | 22mm | 22mm
BS10 Table D | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 1/2" | 9/16" / 14mm | 5/8" / 16mm | 3/8" / 10mm | 1/2" / 13mm
BS10 Table E | 5 1/4" / 133mm | 3 7/8" / 98mm | 4 | 1/2" | 9/16" / 14mm | 5/8" / 16mm | 3/8" / 10mm | 1/2" / 13mm
BS10 Table F | 5 1/2" / 140mm | 4 1/8" / 105mm | 4 | 5/8" | 11/16" / 17mm | 5/8" / 16mm | 7/16" / 11mm | 1/2" / 13mm
BS10 Table H | 5 1/2" / 140mm | 4 1/8" / 105mm | 4 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 1/2" / 13mm | 11/16" / 17mm
BS10 Table J | 5 1/2" / 140mm | 4 1/8" / 105mm | 4 | 5/8" | 11/16" / 17mm |  | 7/8" / 22mm | 7/8" / 22mm
BS10 Table K | 6" / 152mm | 4 1/2" / 114mm | 4 | 3/4" | 7/8" / 22mm |  | 1" / 25mm | 1" / 25mm
BS4504-6 | 130mm | 100mm | 4 | M12 | 14mm | 16mm
BS4504-10 | 150mm | 110mm | 4 | M16 | 18mm | 18mm
BS4504-16 | 150mm | 110mm | 4 | M16 | 18mm | 18mm | 9mm | 18mm
BS4504-25 | 150mm | 110mm | 4 | M16 | 18mm | 20mm | 11mm | 18mm
BS4504-40 | 150mm | 110mm | 4 | M16 | 18mm |  | 13mm | 18mm
BS4504-64 | 170mm | 125mm | 4 | M20 | 22mm |  |  | 28mm
BS4504-100 | 170mm | 125mm | 4 | M20 | 22mm |  |  | 28mm

## DN50
Return To Index Page
Size = DN50
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 6" / 152mm | 4 3/4" / 121mm | 4 | 5/8" | 3/4" / 19mm | 5/8" / 16mm | 1/2" / 13mm | 5/8" / 16mm
ANSI 300 | 6 1/2" / 165mm | 5" / 127mm | 8 | 5/8" | 3/4" / 19mm |  | 3/4" / 19mm | 7/8" / 22mm
ANSI 600 | 6 1/2" / 165mm | 5" / 127mm | 8 | 5/8" | 3/4" / 19mm |  |  | 1" / 25mm
ANSI 900 | 8 1/2" / 216mm | 6 1/2" / 165mm | 8 | 7/8" | 1" / 25mm |  |  | 1 1/2" / 38mm
ANSI 1500 | 8 1/2" / 216mm | 6 1/2" / 165mm | 8 | 7/8" | 1" / 25mm |  |  | 1 1/2" / 38mm
AS2129 Table C | 150mm | 114mm | 4 | 16mm | 18mm | 19mm | 19mm | 14mm
AS2129 Table D | 150mm | 114mm | 4 | 16mm | 18mm | 17mm | 10mm | 14mm
AS2129 Table E | 150mm | 114mm | 4 | 16mm | 18mm | 19mm | 10mm | 14mm
AS2129 Table F | 165mm | 127mm | 4 | 16mm | 18mm | 19mm | 11mm | 16mm
AS2129 Table H | 165mm | 127mm | 4 | 16mm | 18mm | 25mm | 16mm | 19mm
AS2129 Table J | 165mm | 127mm | 4 | 19mm | 22mm |  | 25mm | 25mm
BS10 Table D | 6" / 152mm | 4 1/2" / 114mm | 4 | 5/8" | 11/16" / 17mm | 11/16" / 17mm | 3/8" / 10mm | 9/16" / 14mm
BS10 Table E | 6" / 152mm | 4 1/2" / 114mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 3/8" / 10mm | 9/16" / 14mm
BS10 Table F | 6 1/2" / 165mm | 5" / 127mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 7/16" / 11mm | 5/8" / 16mm
BS10 Table H | 6 1/2" / 165mm | 5" / 127mm | 4 | 5/8" | 11/16" / 17mm | 1" / 25mm | 1/2" / 13mm | 3/4" / 19mm
BS10 Table J | 6 1/2" / 165mm | 5" / 127mm | 4 | 3/4" | 7/8" / 22mm |  | 1" / 25mm | 1" / 25mm
BS10 Table K | 6 1/2" / 165mm | 5" / 127mm | 8 | 5/8" | 11/16" / 17mm |  | 1" / 25mm | 1" / 25mm
BS4504-6 | 140mm | 110mm | 4 | M12 | 14mm | 16mm
BS4504-10 | 165mm | 125mm | 4 | M16 | 18mm | 20mm
BS4504-16 | 165mm | 125mm | 4 | M16 | 18mm | 20mm | 11mm | 20mm
BS4504-25 | 165mm | 125mm | 4 | M16 | 18mm | 22mm | 11mm | 20mm
BS4504-40 | 165mm | 125mm | 4 | M16 | 18mm |  | 13mm | 20mm
BS4504-64 | 180mm | 135mm | 4 | M20 | 22mm |  |  | 26mm
BS4504-100 | 195mm | 145mm | 4 | M24 | 26mm |  |  | 30mm

## DN65
Return To Index Page
Size = DN65
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 7" / 178mm | 5 1/2" / 140mm | 4 | 5/8" | 3/4" / 19mm | 11/16" / 17mm | 9/16" / 14mm | 11/16" / 17mm
ANSI 300 | 7 1/2" / 191mm | 5 7/8" / 149mm | 8 | 3/4" | 7/8" / 22mm |  | 13/16" / 21mm | 1" / 25mm
ANSI 600 | 7 1/2" / 191mm | 5 7/8" / 149mm | 8 | 3/4" | 7/8" / 22mm |  |  | 1 1/8" / 29mm
ANSI 900 | 9 5/8" / 244mm | 7 1/2" / 191mm | 8 | 1" | 1 1/8" / 29mm |  |  | 1 5/8" / 41mm
ANSI 1500 | 9 5/8" / 244mm | 7 1/2" / 191mm | 8 | 1" | 1 1/8" / 29mm |  |  | 1 5/8" / 41mm
AS2129 Table C | 165mm | 127mm | 4 | 16mm | 18mm | 19mm | 19mm | 14mm
AS2129 Table D | 165mm | 127mm | 4 | 16mm | 18mm | 17mm | 11mm | 14mm
AS2129 Table E | 165mm | 127mm | 4 | 16mm | 18mm | 19mm | 11mm | 14mm
AS2129 Table F | 185mm | 146mm | 8 | 16mm | 18mm | 19mm | 13mm | 16mm
AS2129 Table H | 185mm | 146mm | 8 | 1mm | 18mm | 25mm | 14mm | 19mm
AS2129 Table J | 185mm | 146mm | 8 | 19mm | 22mm |  | 25mm | 25mm
BS10 Table D | 6 1/2" / 165mm | 5" / 127mm | 4 | 5/8" | 11/16" / 17mm | 11/16" / 17mm | 7/16" / 11mm | 9/16" / 14mm
BS10 Table E | 6 1/2" / 165mm | 5" / 127mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 7/16" / 11mm | 9/16" / 14mm
BS10 Table F | 7 1/4" / 184mm | 5 3/4" / 146mm | 8 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 1/2" / 13mm | 5/8" / 16mm
BS10 Table H | 7 1/4" / 184mm | 5 3/4" / 146mm | 8 | 5/8" | 11/16" / 17mm | 1" / 25mm | 9/16" / 14mm | 3/4" / 19mm
BS10 Table J | 7 1/4" / 184mm | 5 3/4" / 146mm | 8 | 3/4" | 7/8" / 22mm |  | 1" / 25mm | 1" / 25mm
BS10 Table K | 7 1/4" / 184mm | 5 3/4" / 146mm | 8 | 3/4" | 7/8" / 22mm |  | 1 1/8" / 29mm | 1 1/8" / 29mm
BS4504-6 | 160mm | 130mm | 4 | M12 | 14mm | 16mm
BS4504-10 | 185mm | 145mm | 4 | M16 | 18mm | 20mm
BS4504-16 | 185mm | 145mm | 4 | M16 | 18mm | 20mm | 13mm | 18mm
BS4504-25 | 185mm | 145mm | 8 | M16 | 18mm | 24mm | 13mm | 22mm
BS4504-40 | 185mm | 145mm | 8 | M16 | 18mm |  | 14mm | 22mm
BS4504-64 | 205mm | 160mm | 8 | M20 | 22mm |  |  | 26mm
BS4504-100 | 220mm | 170mm | 8 | M24 | 26mm |  |  | 34mm

## DN80
Return To Index Page
Size = DN80
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 7 1/2" / 191mm | 6" / 152mm | 4 | 5/8" | 3/4" / 19mm | 3/4" / 19mm | 5/8" / 16mm | 3/4" / 19mm
ANSI 300 | 8 1/4" / 210mm | 6 5/8" / 168mm | 8 | 3/4" | 7/8" / 22mm |  | 29/32" / 23mm | 1 1/8" / 29mm
ANSI 600 | 8 1/4" / 210mm | 6 5/8" / 168mm | 8 | 3/4" | 7/8" / 22mm |  |  | 1 1/4" / 32mm
ANSI 900 | 9 1/2" / 241mm | 7 1/2" / 191mm | 8 | 7/8" | 1" / 25mm |  |  | 1 1/2" / 38mm
ANSI 1500 | 10 1/2" / 267mm | 8" / 203mm | 8 | 1 1/8" | 1 1/4" / 32mm |  |  | 1 7/8" / 48mm
AS2129 Table C | 185mm | 146mm | 4 | 16mm | 18mm | 19mm | 19mm | 14mm
AS2129 Table D | 185mm | 146mm | 4 | 16mm | 18mm | 19mm | 13mm | 14mm
AS2129 Table E | 185mm | 146mm | 4 | 16mm | 18mm | 19mm | 13mm | 14mm
AS2129 Table F | 205mm | 165mm | 8 | 16mm | 18mm | 19mm | 14mm | 16mm
AS2129 Table H | 205mm | 165mm | 8 | 16mm | 18mm | 29mm | 16mm | 22mm
AS2129 Table J | 205mm | 165mm | 8 | 19mm | 22mm |  | 32mm | 32mm
BS10 Table D | 7 1/4" / 184mm | 5 3/4" / 146mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 1/2" / 13mm | 9/16" / 14mm
BS10 Table E | 7 1/4" / 184mm | 5 3/4" / 146mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 1/2" / 13mm | 9/16" / 14mm
BS10 Table F | 8" / 203mm | 6 1/2" / 165mm | 8 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 9/16" / 14mm | 5/8" / 16mm
BS10 Table H | 8" / 203mm | 6 1/2" / 165mm | 8 | 5/8" | 11/16" / 17mm | 1 1/8" / 29mm | 5/8" / 16mm | 7/8" / 22mm
BS10 Table J | 8" / 203mm | 6 1/2" / 165mm | 8 | 3/4" | 7/8" / 22mm |  | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table K | 8" / 203mm | 6 1/2" / 165mm | 8 | 3/4" | 7/8" / 22mm |  | 1 1/4" / 32mm | 1 1/4" / 32mm
BS4504-6 | 190mm | 150mm | 4 | M16 | 18mm | 18mm
BS4504-10 | 200mm | 160mm | 8 | M16 | 18mm | 22mm
BS4504-16 | 200mm | 160mm | 8 | M16 | 18mm | 22mm | 13mm | 20mm
BS4504-25 | 200mm | 160mm | 8 | M16 | 18mm | 26mm | 14mm | 24mm
BS4504-40 | 200mm | 160mm | 8 | M16 | 18mm |  | 16mm | 24mm
BS4504-64 | 215mm | 170mm | 8 | M20 | 22mm |  |  | 28mm
BS4504-100 | 230mm | 180mm | 8 | M24 | 26mm |  |  | 36mm

## DN100
Return To Index Page
Size = DN100
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 9" / 229mm | 7 1/2" / 191mm | 8 | 5/8" | 3/4" / 19mm | 15/16" / 24mm | 11/16" / 17mm | 15/16" / 24mm
ANSI 300 | 10" / 254mm | 7 7/8" / 200mm | 8 | 3/4" | 7/8" / 22mm |  | 1 1/16" / 27mm | 1 1/4" / 32mm
ANSI 600 | 10 3/4" / 273mm | 8 1/2" / 216mm | 8 | 7/8" | 1" / 25mm |  |  | 1 1/2" / 38mm
ANSI 900 | 11 1/2" / 292mm | 9 1/4" / 235mm | 8 | 1 1/8" | 1 1/4" / 32mm |  |  | 1 3/4" / 44mm
ANSI 1500 | 12 1/4" / 311mm | 9 1/2" / 241mm | 8 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 1/8" / 54mm
AS2129 Table C | 215mm | 189mm | 4 | 16mm | 18mm | 22mm | 22mm | 17mm
AS2129 Table D | 215mm | 178mm | 4 | 16mm | 18mm | 19mm | 16mm | 17mm
AS2129 Table E | 215mm | 178mm | 8 | 16mm | 18mm | 22mm | 16mm | 17mm
AS2129 Table F | 230mm | 191mm | 8 | 16mm | 18mm | 22mm | 17mm | 19mm
AS2129 Table H | 230mm | 191mm | 8 | 16mm | 18mm | 32mm | 19mm | 25mm
AS2129 Table J | 230mm | 191mm | 8 | 19mm | 22mm |  | 35mm | 35mm
BS10 Table D | 8 1/2" / 216mm | 7" / 178mm | 4 | 5/8" | 11/16" / 17mm | 3/4" / 19mm | 5/8" / 16mm | 11/16" / 17mm
BS10 Table E | 8 1/2" / 216mm | 7" / 178mm | 8 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 5/8" / 16mm | 11/16" / 17mm
BS10 Table F | 9" / 229mm | 7 1/2" / 191mm | 8 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 11/16" / 17mm | 3/4" / 19mm
BS10 Table H | 9" / 229mm | 7 1/2" / 191mm | 8 | 5/8" | 11/16" / 17mm | 1 1/4" / 32mm | 3/4" / 19mm | 1" / 25mm
BS10 Table J | 9" / 229mm | 7 1/2" / 191mm | 8 | 3/4" | 7/8" / 22mm |  | 1 3/8" / 35mm | 1 3/8" / 35mm
BS10 Table K | 9 1/2" / 241mm | 7 3/4" / 197mm | 8 | 7/8" | 1" / 25mm |  | 1 3/8" / 35mm | 1 3/8" / 35mm
BS4504-6 | 210mm | 170mm | 4 | M16 | 18mm | 18mm
BS4504-10 | 220mm | 180mm | 8 | M16 | 18mm | 24mm
BS4504-16 | 220mm | 180mm | 8 | M16 | 18mm | 24mm | 16mm | 20mm
BS4504-25 | 235mm | 190mm | 8 | M20 | 22mm | 28mm | 17mm | 24mm
BS4504-40 | 235mm | 190mm | 8 | M20 | 22mm |  | 19mm | 24mm
BS4504-64 | 250mm | 200mm | 8 | M24 | 26mm |  |  | 30mm
BS4504-100 | 265mm | 210mm | 8 | M27 | 30mm |  |  | 40mm

## DN125
Return To Index Page
Size = DN125
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 10" / 254mm | 8 1/2" / 216mm | 8 | 3/4" | 7/8" / 22mm | 15/16" / 24mm | 3/4" / 19mm | 15/16" / 24mm
ANSI 300 | 11" / 279mm | 9 1/4" / 235mm | 8 | 3/4" | 7/8" / 22mm |  | 1 1/8" / 29mm | 1 3/8" / 35mm
ANSI 600 | 13" / 330mm | 10 1/2" / 267mm | 8 | 1" | 1 1/8" / 29mm |  |  | 1 3/4" / 44mm
ANSI 900 | 13 3/4" / 349mm | 11" / 279mm | 8 | 1 1/4" | 1 3/8" / 35mm |  |  | 2" / 51mm
ANSI 1500 | 14 3/4" / 375mm | 11 1/2" / 292mm | 8 | 1 1/2" | 1 5/8" / 41mm |  |  | 2 7/8" / 73mm
AS2129 Table C | 255mm | 210mm | 8 | 16mm | 18mm | 22mm | 22mm | 17mm
AS2129 Table D | 255mm | 210mm | 8 | 16mm | 18mm | 21mm | 17mm | 17mm
AS2129 Table E | 255mm | 210mm | 8 | 16mm | 18mm | 22mm | 17mm | 17mm
AS2129 Table F | 280mm | 235mm | 8 | 19mm | 22mm | 25mm | 19mm | 22mm
AS2129 Table H | 280mm | 235mm | 8 | 19mm | 22mm | 35mm | 22mm | 29mm
AS2129 Table J | 280mm | 235mm | 8 | 22mm | 26mm |  | 22mm | 26mm
BS10 Table D | 10" / 254mm | 8 1/4" / 210mm | 8 | 5/8" | 11/16" / 17mm | 13/16" / 21mm | 11/16" / 17mm | 11/16" / 17mm
BS10 Table E | 10" / 254mm | 8 1/4" / 210mm | 8 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 11/16" / 17mm | 11/16" / 17mm
BS10 Table F | 11" / 279mm | 9 1/4" / 235mm | 8 | 3/4" | 7/8" / 22mm | 1" / 25mm | 3/4" / 19mm | 7/8" / 22mm
BS10 Table H | 11" / 279mm | 9 1/4" / 235mm | 8 | 3/4" | 7/8" / 22mm | 1 3/8" / 35mm | 7/8" / 22mm | 1 1/8" / 29mm
BS10 Table J | 11" / 279mm | 9 1/4" / 235mm | 8 | 7/8" | 1" / 25mm |  | 1 1/2" / 38mm | 1 1/2" / 38mm
BS10 Table K | 11" / 279mm | 9 1/4" / 235mm | 12 | 7/8" | 1" / 25mm |  | 1 5/8" / 41mm | 1 5/8" / 41mm
BS4504-6 | 240mm | 200mm | 8 | M16 | 18mm | 20mm
BS4504-10 | 250mm | 210mm | 8 | M16 | 18mm | 26mm
BS4504-16 | 250mm | 210mm | 8 | M16 | 18mm | 26mm |  | 22mm
BS4504-25 | 270mm | 220mm | 8 | M24 | 26mm | 30mm |  | 26mm
BS4504-40 | 270mm | 220mm | 8 | M24 | 26mm |  |  | 26mm
BS4504-64 | 295mm | 240mm | 8 | M27 | 30mm |  |  | 34mm
BS4504-100 | 315mm | 250mm | 8 | M30 | 33mm |  |  | 40mm

## DN150
Return To Index Page
Size = DN150
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 11" / 279mm | 9 1/2" / 241mm | 8 | 3/4" | 7/8" / 22mm | 1" / 25mm | 13/16" / 21mm | 1" / 25mm
ANSI 300 | 12 1/2" / 318mm | 10 5/8" / 270mm | 12 | 3/4" | 7/8" / 22mm |  | 1 3/16" / 30mm | 1 7/16" / 37mm
ANSI 600 | 14" / 356mm | 11 1/2" / 292mm | 12 | 1" | 1 1/8" / 29mm |  |  | 1 7/8" / 48mm
ANSI 900 | 15" / 381mm | 12 1/2" / 318mm | 12 | 1 1/8" | 1 1/4" / 32mm |  |  | 2 3/16" / 56mm
ANSI 1500 | 15 1/2" / 394mm | 12 1/2" / 318mm | 12 | 1 3/8" | 1 1/2" / 38mm |  |  | 3 1/4" / 83mm
AS2129 Table C | 280mm | 235mm | 8 | 16mm | 18mm | 22mm | 22mm | 17mm
AS2129 Table D | 280mm | 235mm | 8 | 16mm | 18mm | 21mm | 17mm | 17mm
AS2129 Table E | 280mm | 235mm | 8 | 19mm | 22mm | 22mm | 17mm | 17mm
AS2129 Table F | 305mm | 260mm | 12 | 19mm | 22mm | 25mm | 22mm | 22mm
AS2129 Table H | 305mm | 260mm | 12 | 19mm | 22mm | 35mm | 25mm | 29mm
AS2129 Table J | 305mm | 260mm | 12 | 22mm | 26mm |  | 38mm | 38mm
BS10 Table D | 11" / 279mm | 9 1/4" / 235mm | 8 | 5/8" | 11/16" / 17mm | 13/16" / 21mm | 11/16" / 17mm | 11/16" / 17mm
BS10 Table E | 11" / 279mm | 9 1/4" / 235mm | 8 | 3/4" | 7/8" / 22mm | 7/8" / 22mm | 11/16" / 17mm | 11/16" / 17mm
BS10 Table F | 12" / 305mm | 10 1/4" / 260mm | 12 | 3/4" | 7/8" / 22mm | 1" / 25mm | 7/8" / 22mm | 7/8" / 22mm
BS10 Table H | 12" / 305mm | 10 1/4" / 260mm | 12 | 3/4" | 7/8" / 22mm | 1 3/8" / 35mm | 1" / 25mm | 1 1/8" / 29mm
BS10 Table J | 12" / 305mm | 10 1/4" / 260mm | 12 | 7/8" | 1" / 25mm |  | 1 1/2" / 38mm | 1 1/2" / 38mm
BS10 Table K | 12" / 305mm | 10 1/4" / 260mm | 12 | 7/8" | 1" / 25mm |  | 1 5/8" / 41mm | 1 5/8" / 41mm
BS4504-6 | 265mm | 225mm | 8 | M16 | 18mm | 20mm
BS4504-10 | 285mm | 240mm | 8 | M20 | 22mm | 26mm
BS4504-16 | 285mm | 240mm | 8 | M20 | 22mm | 26mm |  | 22mm
BS4504-25 | 300mm | 250mm | 8 | M24 | 26mm | 34mm |  | 28mm
BS4504-40 | 300mm | 250mm | 8 | M24 | 26mm |  |  | 28mm
BS4504-64 | 345mm | 280mm | 8 | M30 | 33mm |  |  | 36mm
BS4504-100 | 355mm | 290mm | 12 | M30 | 33mm |  |  | 44mm

## DN200
Return To Index Page
Size = DN200
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 13 1/2" / 343mm | 11 3/4" / 298mm | 8 | 3/4" | 7/8" / 22mm | 1 1/8" / 29mm | 15/16" / 24mm | 1 1/8" / 29mm
ANSI 300 | 15" / 381mm | 13" / 330mm | 12 | 7/8" | 1" / 25mm |  | 1 3/8" / 35mm | 1 5/8" / 41mm
ANSI 600 | 16 1/2" / 419mm | 13 3/4" / 349mm | 12 | 1 1/8" | 1 1/4" / 32mm |  |  | 2 3/16" / 56mm
ANSI 900 | 18 1/2" / 470mm | 15 1/2" / 394mm | 12 | 1 3/8" | 1 1/2" / 38mm |  |  | 2 1/2" / 64mm
ANSI 1500 | 19" / 483mm | 15 1/2" / 394mm | 12 | 1 5/8" | 1 3/4" / 44mm |  |  | 3 5/8" / 92mm
AS2129 Table C | 335mm | 292mm | 8 | 16mm | 18mm | 25mm | 25mm | 19mm
AS2129 Table D | 335mm | 292mm | 8 | 16mm | 18mm | 22mm | 19mm | 19mm
AS2129 Table E | 335mm | 292mm | 8 | 19mm | 22mm | 25mm | 19mm | 19mm
AS2129 Table F | 370mm | 324mm | 12 | 19mm | 22mm | 29mm | 25mm | 25mm
AS2129 Table H | 370mm | 324mm | 12 | 19mm | 22mm | 38mm | 32mm | 32mm
AS2129 Table J | 370mm | 324mm | 12 | 22mm | 26mm |  | 41mm | 41mm
BS10 Table D | 13 1/4" / 337mm | 11 1/2" / 292mm | 8 | 5/8" | 11/16" / 17mm | 7/8" / 22mm | 3/4" / 19mm | 3/4" / 19mm
BS10 Table E | 13 1/4" / 337mm | 11 1/2" / 292mm | 8 | 3/4" | 7/8" / 22mm | 1" / 25mm | 3/4" / 19mm | 3/4" / 19mm
BS10 Table F | 14 1/2" / 368mm | 12 3/4" / 324mm | 12 | 3/4" | 7/8" / 22mm | 1 1/8" / 29mm | 1" / 25mm | 1" / 25mm
BS10 Table H | 14 1/2" / 368mm | 12 3/4" / 324mm | 12 | 3/4" | 7/8" / 22mm | 1 1/2" / 38mm | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table J | 14 1/2" / 368mm | 12 3/4" / 324mm | 12 | 7/8" | 1" / 25mm |  | 1 5/8" / 41mm | 1 5/8" / 41mm
BS10 Table K | 14 1/2" / 368mm | 12 1/2" / 318mm | 12 | 1" | 1 1/8" / 29mm |  | 1 7/8" / 48mm | 1 7/8" / 48mm
BS4504-6 | 320mm | 280mm | 8 | M16 | 18mm | 22mm
BS4504-10 | 340mm | 295mm | 8 | M20 | 22mm | 26mm
BS4504-16 | 340mm | 295mm | 12 | M20 | 22mm | 30mm |  | 24mm
BS4504-25 | 360mm | 310mm | 12 | M24 | 26mm | 34mm |  | 30mm
BS4504-40 | 375mm | 320mm | 12 | M27 | 30mm |  |  | 34mm
BS4504-64 | 415mm | 345mm | 12 | M33 | 36mm |  |  | 42mm
BS4504-100 | 430mm | 360mm | 12 | M33 | 36mm |  |  | 52mm

## DN250
Return To Index Page
Size = DN250
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 16" / 406mm | 14 1/4" / 362mm | 12 | 7/8" | 1" / 25mm | 1 3/16" / 30mm | 1" / 25mm | 1 3/16" / 30mm
ANSI 300 | 17 1/2" / 445mm | 15 1/4" / 387mm | 16 | 1" | 1 1/8" / 29mm |  |  | 1 7/8" / 48mm
ANSI 600 | 20" / 508mm | 17" / 432mm | 16 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 1/2" / 64mm
ANSI 900 | 21 1/2" / 546mm | 18 1/2" / 470mm | 16 | 1 3/8" | 1 1/2" / 38mm |  |  | 2 3/4" / 70mm
ANSI 1500 | 23" / 584mm | 19" / 483mm | 12 | 1 7/8" | 2" / 51mm |  |  | 4 1/4" / 108mm
AS2129 Table C | 405mm | 356mm | 8 | 19mm | 22mm | 25mm | 25mm | 19mm
AS2129 Table D | 405mm | 356mm | 8 | 19mm | 22mm | 25mm | 19mm | 19mm
AS2129 Table E | 405mm | 356mm | 12 | 19mm | 22mm | 25mm | 22mm | 22mm
AS2129 Table F | 430mm | 381mm | 12 | 22mm | 26mm | 29mm | 25mm | 25mm
AS2129 Table H | 430mm | 381mm | 12 | 22mm | 26mm | 41mm | 35mm | 35mm
AS2129 Table J | 430mm | 381mm | 12 | 25mm | 30mm |  |  | 48mm
BS10 Table D | 16" / 406mm | 14" / 356mm | 8 | 3/4" | 7/8" / 22mm | 1" / 25mm | 3/4" / 19mm | 3/4" / 19mm
BS10 Table E | 16" / 406mm | 14" / 356mm | 12 | 3/4" | 7/8" / 22mm | 1" / 25mm | 7/8" / 22mm | 7/8" / 22mm
BS10 Table F | 17" / 432mm | 15" / 381mm | 12 | 7/8" | 1" / 25mm | 1 1/8" / 29mm | 1" / 25mm | 1" / 25mm
BS10 Table H | 17" / 432mm | 15" / 381mm | 12 | 7/8" | 1" / 25mm | 1 5/8" / 41mm | 1 3/8" / 35mm | 1 3/8" / 35mm
BS10 Table J | 17" / 432mm | 15" / 381mm | 12 | 1" | 1 1/8" / 29mm |  |  | 1 7/8" / 48mm
BS10 Table K | 17" / 432mm | 15" / 381mm | 16 | 1" | 1 1/8" / 29mm |  |  | 2" / 51mm
BS4504-6 | 375mm | 335mm | 12 | M16 | 18mm | 24mm
BS4504-10 | 395mm | 350mm | 12 | M20 | 22mm | 28mm
BS4504-16 | 405mm | 355mm | 12 | M24 | 26mm | 32mm |  | 26mm
BS4504-25 | 425mm | 370mm | 12 | M27 | 30mm | 36mm |  | 32mm
BS4504-40 | 450mm | 385mm | 12 | M30 | 33mm |  |  | 38mm
BS4504-64 | 470mm | 400mm | 12 | M33 | 36mm |  |  | 46mm
BS4504-100 | 505mm | 430mm | 12 | M36 | 39mm |  |  | 60mm

## DN300
Return To Index Page
Size = DN300
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 19" / 483mm | 17" / 432mm | 12 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1 1/16" / 27mm | 1 1/4" / 32mm
ANSI 300 | 20 1/2" / 521mm | 17 3/4" / 451mm | 16 | 1 1/8" | 1 1/4" / 32mm |  |  | 2" / 51mm
ANSI 600 | 22" / 559mm | 19 1/4" / 489mm | 20 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 5/8" / 67mm
ANSI 900 | 24" / 610mm | 21" / 533mm | 20 | 1 3/8" | 1 1/2" / 38mm |  |  | 3 1/8" / 79mm
ANSI 1500 | 26 1/2" / 673mm | 22 1/2" / 572mm | 16 | 2" | 2 1/8" / 54mm |  |  | 4 7/8" / 124mm
AS2129 Table C | 455mm | 406mm | 12 | 19mm | 22mm | 29mm | 29mm | 22mm
AS2129 Table D | 455mm | 406mm | 12 | 19mm | 22mm | 25mm | 22mm | 22mm
AS2129 Table E | 455mm | 406mm | 12 | 22mm | 26mm | 29mm | 25mm | 25mm
AS2129 Table F | 490mm | 438mm | 16 | 22mm | 26mm | 32mm | 29mm | 29mm
AS2129 Table H | 490mm | 438mm | 16 | 22mm | 26mm | 44mm | 38mm | 38mm
AS2129 Table J | 490mm | 438mm | 16 | 25mm | 30mm |  |  | 51mm
BS10 Table D | 18" / 457mm | 16" / 406mm | 12 | 3/4" | 7/8" / 22mm | 1" / 25mm | 7/8" / 22mm | 7/8" / 22mm
BS10 Table E | 18" / 457mm | 16" / 406mm | 12 | 7/8" | 1" / 25mm | 1 1/8" / 29mm | 1" / 25mm | 1" / 25mm
BS10 Table F | 19 1/4" / 489mm | 17 1/4" / 438mm | 16 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1 1/8" / 29mm | 1 1/8" / 29mm
BS10 Table H | 19 1/4" / 489mm | 17 1/4" / 438mm | 16 | 7/8" | 1" / 25mm | 1 3/4" / 44mm | 1 1/2" / 38mm | 1 1/2" / 38mm
BS10 Table J | 19 1/4" / 489mm | 17 1/4" / 438mm | 16 | 1" | 1 1/8" / 29mm |  |  | 2" / 51mm
BS10 Table K | 19 1/4" / 489mm | 17" / 432mm | 16 | 1 1/8" | 1 1/4" / 32mm |  |  | 1 1/4" / 32mm
BS4504-6 | 440mm | 395mm | 12 | M20 | 22mm | 24mm
BS4504-10 | 445mm | 400mm | 12 | M20 | 22mm | 28mm
BS4504-16 | 460mm | 410mm | 12 | M24 | 26mm | 32mm |  | 28mm
BS4504-25 | 485mm | 430mm | 16 | M27 | 30mm | 40mm |  | 34mm
BS4504-40 | 515mm | 450mm | 16 | M30 | 33mm |  |  | 42mm
BS4504-64 | 530mm | 460mm | 16 | M33 | 36mm |  |  | 52mm
BS4504-100 | 585mm | 500mm | 16 | M39 | 42mm |  |  | 68mm

## DN350
Return To Index Page
Size = DN350
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 21" / 533mm | 18 3/4" / 476mm | 12 | 1" | 1 1/8" / 29mm | 1 3/8" / 35mm |  | 1 3/8" / 35mm
ANSI 300 | 23" / 584mm | 20 1/4" / 514mm | 20 | 1 1/8" | 1 1/4" / 32mm |  |  | 2 1/8" / 54mm
ANSI 600 | 23 3/4" / 603mm | 20 3/4" / 527mm | 20 | 1 3/8" | 1 1/2" / 38mm |  |  | 2 3/4" / 70mm
ANSI 900 | 25 1/4" / 641mm | 22" / 559mm | 20 | 1 1/2" | 1 5/8" / 41mm |  |  | 3 3/8" / 86mm
ANSI 1500 | 29 1/2" / 749mm | 25" / 635mm | 16 | 2 1/4" | 2 3/8" / 60mm |  |  | 5 1/4" / 133mm
AS2129 Table C | 525mm | 470mm | 12 | 22mm | 26mm | 32mm | 32mm | 25mm
AS2129 Table D | 525mm | 470mm | 12 | 22mm | 26mm | 29mm | 25mm | 25mm
AS2129 Table E | 525mm | 470mm | 12 | 22mm | 26mm | 32mm | 25mm | 25mm
AS2129 Table F | 550mm | 495mm | 16 | 25mm | 30mm | 35mm | 32mm | 32mm
AS2129 Table H | 550mm | 495mm | 16 | 5mm | 30mm | 48mm | 41mm | 41mm
AS2129 Table J | 550mm | 495mm | 16 | 29mm | 33mm |  |  | 54mm
BS10 Table D | 20 3/4" / 527mm | 18 1/2" / 470mm | 12 | 7/8" | 1" / 25mm | 1 1/8" / 29mm | 1" / 25mm | 1" / 25mm
BS10 Table E | 20 3/4" / 527mm | 18 1/2" / 470mm | 12 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1" / 25mm | 1" / 25mm
BS10 Table F | 21 3/4" / 552mm | 19 1/2" / 495mm | 16 | 1" | 1 1/8" / 29mm | 1 3/8" / 35mm | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table H | 21 3/4" / 552mm | 19 1/2" / 495mm | 16 | 1" | 1 1/8" / 29mm | 1 7/8" / 48mm | 1 5/8" / 41mm | 1 5/8" / 41mm
BS10 Table J | 21 3/4" / 552mm | 19 1/2" / 495mm | 16 | 1 1/8" | 1 1/4" / 32mm |  |  | 2 1/8" / 54mm
BS10 Table K | 22 1/2" / 572mm | 20" / 508mm | 16 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 3/8" / 60mm
BS4504-6 | 490mm | 445mm | 12 | M20 | 22mm | 26mm
BS4504-10 | 505mm | 460mm | 16 | M20 | 22mm | 30mm
BS4504-16 | 520mm | 470mm | 16 | M24 | 26mm | 36mm |  | 30mm
BS4504-25 | 555mm | 490mm | 16 | M30 | 33mm | 44mm |  | 38mm
BS4504-40 | 580mm | 510mm | 16 | M33 | 36mm |  |  | 46mm
BS4504-64 | 600mm | 525mm | 16 | M36 | 39mm |  |  | 56mm
BS4504-100 | 655mm | 560mm | 16 | M45 | 48mm |  |  | 74mm

## DN375
Return To Index Page
Size = DN375
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
BS10 Table D | 21 3/4" / 552mm | 21 3/4" / 552mm | 12 | 7/8" | 1" / 25mm | 1 1/8" / 29mm | 1" / 25mm
BS10 Table E | 21 3/4" / 552mm | 21 3/4" / 552mm | 12 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1" / 25mm
BS10 Table F | 22 3/4" / 578mm | 22 3/4" / 578mm | 16 | 1" | 1 1/8" / 29mm | 1 3/8" / 35mm | 1 1/4" / 32mm
BS10 Table H | 22 3/4" / 578mm | 22 3/4" / 578mm | 16 | 1" | 1 1/8" / 29mm | 2" / 51mm | 1 3/4" / 44mm
BS10 Table J | 22 3/4" / 578mm | 22 3/4" / 578mm | 16 | 1 1/8" | 1 1/4" / 32mm
BS10 Table K | 33 3/4" / 857mm | 23 3/4" / 603mm | 20 | 1 1/4" | 1 3/8" / 35mm

## DN400
Return To Index Page
Size = DN400
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 23 1/2" / 597mm | 21 1/4" / 540mm | 16 | 1" | 1 1/8" / 29mm | 1 7/16" / 37mm |  | 1 7/16" / 37mm
ANSI 300 | 25 1/2" / 648mm | 22 1/2" / 572mm | 20 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 1/4" / 57mm
ANSI 600 | 27 1/2" / 699mm | 23 3/4" / 603mm | 20 | 1 1/2" | 1 5/8" / 41mm |  |  | 3" / 76mm
ANSI 900 | 27 3/4" / 705mm | 24 1/4" / 616mm | 20 | 1 5/8" | 1 3/4" / 44mm |  |  | 3 1/2" / 89mm
ANSI 1500 | 32 1/2" / 826mm | 27 3/4" / 705mm | 16 | 2 1/2" | 2 5/8" / 67mm |  |  | 5 3/4" / 146mm
AS2129 Table C | 580mm | 521mm | 12 | 22mm | 26mm | 32mm | 32mm | 25mm
AS2129 Table D | 580mm | 521mm | 12 | 22mm | 26mm | 29mm | 25mm | 25mm
AS2129 Table E | 580mm | 521mm | 12 | 22mm | 26mm | 32mm | 25mm | 25mm
AS2129 Table F | 610mm | 552mm | 20 | 25mm | 30mm | 35mm | 32mm | 32mm
AS2129 Table H | 610mm | 552mm | 20 | 25mm | 30mm | 51mm | 44mm | 44mm
AS2129 Table J | 610mm | 552mm | 20 | 29mm | 33mm |  |  | 57mm
BS10 Table D | 22 3/4" / 578mm | 20 1/2" / 521mm | 12 | 7/8" | 1" / 25mm | 1 1/8" / 29mm | 1" / 25mm | 1" / 25mm
BS10 Table E | 22 3/4" / 578mm | 20 1/2" / 521mm | 12 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1" / 25mm | 1" / 25mm
BS10 Table F | 24" / 610mm | 21 3/4" / 552mm | 20 | 1" | 1 1/8" / 29mm | 1 3/8" / 35mm | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table H | 24" / 610mm | 21 3/4" / 552mm | 20 | 1" | 1 1/8" / 29mm | 2" / 51mm | 1 3/4" / 44mm | 1 3/4" / 44mm
BS10 Table J | 24" / 610mm | 21 3/4" / 552mm | 20 | 1 1/8" | 1 1/4" / 32mm |  |  | 2 1/4" / 57mm
BS10 Table K | 24 3/4" / 629mm | 22 1/4" / 565mm | 20 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 5/8" / 67mm
BS4504-6 | 540mm | 495mm | 16 | M20 | 22mm | 28mm
BS4504-10 | 565mm | 515mm | 16 | M24 | 26mm | 32mm
BS4504-16 | 580mm | 525mm | 16 | M27 | 30mm | 38mm |  | 32mm
BS4504-25 | 620mm | 550mm | 16 | M33 | 36mm | 48mm |  | 40mm
BS4504-40 | 660mm | 585mm | 16 | M36 | 39mm |  |  | 50mm
BS4504-64 | 670mm | 585mm | 16 | M39 | 42mm |  |  | 60mm
BS4504-100 | 715mm | 620mm | 16 | M45 | 48mm |  |  | 78mm

## DN450
Return To Index Page
Size = DN450
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 25" / 635mm | 22 3/4" / 578mm | 16 | 1 1/8" | 1 1/4" / 32mm | 1 9/16" / 40mm |  | 1 9/16" / 40mm
ANSI 300 | 28" / 711mm | 24 3/4" / 629mm | 24 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 3/8" / 60mm
ANSI 600 | 29 1/4" / 743mm | 25 3/4" / 654mm | 20 | 1 5/8" | 1 3/4" / 44mm |  |  | 3 1/4" / 83mm
ANSI 900 | 31" / 787mm | 27" / 686mm | 20 | 1 7/8" | 2" / 51mm |  |  | 4" / 102mm
ANSI 1500 | 36" / 914mm | 30 1/2" / 775mm | 16 | 2 3/4" | 2 7/8" / 73mm |  |  | 6 3/8" / 162mm
AS2129 Table C | 640mm | 584mm | 12 | 22mm | 26mm | 35mm | 35mm | 29mm
AS2129 Table D | 640mm | 584mm | 12 | 22mm | 26mm | 32mm | 29mm | 29mm
AS2129 Table E | 640mm | 584mm | 16 | 22mm | 26mm | 35mm | 29mm | 29mm
AS2129 Table F | 675mm | 610mm | 20 | 29mm | 33mm | 38mm | 35mm | 35mm
AS2129 Table H | 675mm | 610mm | 20 | 29mm | 33mm | 54mm | 48mm | 48mm
AS2129 Table J | 675mm | 610mm | 20 | 32mm | 35mm |  |  | 60mm
BS10 Table D | 25 1/4" / 641mm | 23" / 584mm | 12 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1 1/8" / 29mm | 1 1/8" / 29mm
BS10 Table E | 25 1/4" / 641mm | 23" / 584mm | 16 | 7/8" | 1" / 25mm | 1 3/8" / 35mm | 1 1/8" / 29mm | 1 1/8" / 29mm
BS10 Table F | 26 1/2" / 673mm | 24" / 610mm | 20 | 1 1/8" | 1 1/4" / 32mm | 1 1/2" / 38mm | 1 3/8" / 35mm | 1 3/8" / 35mm
BS10 Table H | 26 1/2" / 673mm | 24" / 610mm | 20 | 1 1/8" | 1 1/4" / 32mm | 2 1/8" / 54mm | 1 7/8" / 48mm | 1 7/8" / 48mm
BS10 Table J | 26 1/2" / 673mm | 24" / 610mm | 20 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 3/8" / 60mm
BS10 Table K | 28 1/4" / 718mm | 25 3/4" / 654mm | 20 | 1 3/8" | 1 1/2" / 38mm |  |  | 3" / 76mm
BS4504-6 | 595mm | 550mm | 16 | M20 | 22mm | 30mm
BS4504-10 | 615mm | 565mm | 20 | M24 | 26mm | 32mm
BS4504-16 | 640mm | 585mm | 20 | M27 | 30mm | 40mm

## DN500
Return To Index Page
Size = DN500
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 27 1/2" / 699mm | 25" / 635mm | 20 | 1 1/8" | 1 1/4" / 32mm | 1 11/16" / 43mm |  | 1 11/16" / 43mm
ANSI 300 | 30 1/2" / 775mm | 27" / 686mm | 24 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 1/2" / 64mm
ANSI 600 | 32" / 813mm | 28 1/2" / 724mm | 24 | 1 5/8" | 1 3/4" / 44mm |  |  | 3 1/2" / 89mm
ANSI 900 | 33 1/4" / 845mm | 29 1/2" / 749mm | 20 | 2" | 2 1/8" / 54mm |  |  | 4 1/4" / 108mm
ANSI 1500 | 38 3/4" / 984mm | 32 3/4" / 832mm | 16 | 3" | 3 1/8" / 79mm |  |  | 7" / 178mm
AS2129 Table C | 705mm | 641mm | 16 | 22mm | 26mm | 38mm | 38mm | 32mm
AS2129 Table D | 705mm | 641mm | 16 | 22mm | 26mm | 32mm | 32mm | 32mm
AS2129 Table E | 705mm | 641mm | 16 | 22mm | 26mm | 38mm | 32mm | 32mm
AS2129 Table F | 735mm | 673mm | 24 | 29mm | 33mm | 41mm | 38mm | 38mm
AS2129 Table H | 735mm | 673mm | 24 | 29mm | 33mm | 57mm | 51mm | 51mm
AS2129 Table J | 735mm | 673mm | 24 | 32mm | 36mm |  |  | 64mm
BS10 Table D | 27 3/4" / 705mm | 25 1/4" / 641mm | 16 | 7/8" | 1" / 25mm | 1 1/4" / 32mm | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table E | 27 3/4" / 705mm | 25 1/4" / 641mm | 16 | 7/8" | 1" / 25mm | 1 1/2" / 38mm | 1 1/4" / 32mm | 1 1/4" / 32mm
BS10 Table F | 29" / 737mm | 26 1/2" / 673mm | 20 | 1 1/8" | 1 1/4" / 32mm | 1 5/8" / 41mm | 1 1/2" / 38mm | 1 1/2" / 38mm
BS10 Table H | 29" / 737mm | 26 1/2" / 673mm | 20 | 1 1/8" | 1 1/4" / 32mm | 2 1/4" / 57mm | 2" / 51mm | 2" / 51mm
BS10 Table J | 29" / 737mm | 26 1/2" / 673mm | 20 | 1 1/4" | 1 3/8" / 35mm |  |  | 2 1/2" / 64mm
BS10 Table K | 31" / 787mm | 28" / 711mm | 20 | 1 1/2" | 1 5/8" / 41mm |  |  | 3 1/4" / 83mm
BS4504-6 | 645mm | 600mm | 20 | M20 | 22mm | 30mm
BS4504-10 | 670mm | 620mm | 20 | M24 | 26mm | 34mm
BS4504-16 | 715mm | 650mm | 20 | M30 | 33mm | 42mm |  | 36mm
BS4504-25 | 730mm | 660mm | 20 | M33 | 36mm | 52mm |  | 44mm
BS4504-40 | 755mm | 670mm | 20 | M39 | 42mm |  |  | 52mm
BS4504-64 | 800mm | 705mm | 20 | M45 | 58mm |  |  | 67mm
BS4504-100 | 870mm | 760mm | 20 | M52 | 56mm |  |  | 94mm

## DN600
Return To Index Page
Size = DN600
Table | Flange | PCD | Bolts | Bolt | Hole Size | Thickness
| Diameter |  |  | Size |  | Grey Cast Iron | Copper Alloy | Cast / Forged Steel
ANSI 125/150 | 32" / 813mm | 29 1/2" / 749mm | 20 | 1 1/4" | 1 3/8" / 35mm | 1 7/8" / 48mm |  | 1 7/8" / 48mm
ANSI 300 | 36" / 914mm | 32" / 813mm | 24 | 1 1/2" | 1 5/8" / 41mm |  |  | 2 3/4" / 70mm
ANSI 600 | 37" / 940mm | 33" / 838mm | 24 | 1 7/8" | 2" / 51mm |  |  | 4" / 102mm
ANSI 900 | 41" / 1041mm | 34" / 864mm | 20 | 2 1/2" | 2 5/8" / 67mm |  |  | 5 1/2" / 140mm
ANSI 1500 | 46" / 1168mm | 39" / 991mm | 16 | 3 1/2" | 3 5/8" / 92mm |  |  | 8" / 203mm
AS2129 Table C | 825mm | 756mm | 16 | 25mm | 30mm | 41mm | 41mm | 35mm
AS2129 Table D | 825mm | 756mm | 16 | 25mm | 30mm | 35mm | 35mm | 35mm
AS2129 Table E | 825mm | 756mm | 16 | 29mm | 33mm | 41mm | 38mm | 38mm
AS2129 Table F | 850mm | 781mm | 24 | 32mm | 36mm | 44mm | 41mm | 41mm
AS2129 Table H | 850mm | 781mm | 24 | 32mm | 36mm | 64mm | 57mm | 57mm
AS2129 Table J | 850mm | 781mm | 24 | 35mm | 39mm |  |  | 70mm
BS10 Table D | 32 1/2" / 826mm | 29 3/4" / 756mm | 16 | 1" | 1 1/8" / 29mm | 1 3/8" / 35mm | 1 3/8" / 35mm | 1 3/8" / 35mm
BS10 Table E | 32 1/2" / 826mm | 29 3/4" / 756mm | 16 | 1 1/8" | 1 1/4" / 32mm | 1 5/8" / 41mm | 1 1/2" / 38mm | 1 1/2" / 38mm
BS10 Table F | 33 1/2" / 851mm | 30 3/4" / 781mm | 24 | 1 1/4" | 1 3/8" / 35mm | 1 3/4" / 44mm | 1 5/8" / 41mm | 1 5/8" / 41mm
BS10 Table H | 33 1/2" / 851mm | 30 3/4" / 781mm | 24 | 1 1/4" | 1 3/8" / 35mm | 2 1/2" / 64mm | 2 1/4" / 57mm | 2 1/4" / 57mm
BS10 Table J | 33 1/2" / 851mm | 30 3/4" / 781mm | 24 | 1 3/8" | 1 1/2" / 38mm |  |  | 2 3/4" / 70mm
BS4504-6 | 755mm | 705mm | 20 | M24 | 26mm | 30mm
BS4504-10 | 780mm | 725mm | 20 | M27 | 30mm | 36mm
BS4504-16 | 840mm | 770mm | 20 | M33 | 36mm | 48mm |  | 40mm
BS4504-25 | 845mm | 770mm | 20 | M36 | 39mm |  |  | 46mm
BS4504-40 | 890mm | 795mm | 20 | M45 | 48mm |  |  | 60mm
BS4504-64 | 930mm | 820mm | 20 | M52 | 56mm |  |  | 76mm
BS4504-100 | 990mm | 875mm | 20 | M56 | 62mm |  |  | 104mm