## Imperial
The purpose of this table is to provide a quick determination of the "worst case" distance a flange extends beyond the pipe O. D. for use during pipe line spacing |  |  |  |  | Quick Worst Case Flange Extension Chart | [11 empty] | The Rule for line spacing is: Flange-to-pipe plus and inch. For the flange you should use the worst case.
All Ratings |  | 150# |  |  | 300# |  |  | 400# |  |  | 600# |  |  | 900# |  |  | 1500# |  |  | 2500#
Nominal Size | Actual Pipe O. D. (Inches) | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension |  | Flange O. D. (Inches) | Flange Extension
3 | 3.5 | 7.5 | 2 | 3.5 | 8.25 | 2.375 | 3.5 | (use 600#) |  | 3.5 | 8.25 | 2.375 | 3.5 | 9.5 | 3 | 3.5 | 10.5 | 3.5 | 3.5 | 12 | 4.25
4 | 4.5 | 9 | 2.25 | 4.5 | 10 | 2.75 | 4.5 | 10 | 2.75 | 4.5 | 10.75 | 3.125 | 4.5 | 11.5 | 3.5 | 4.5 | 12.25 | 3.875 | 4.5 | 14 | 4.75
6 | 6.625 | 11 | 2.1875 | 6.625 | 12.5 | 2.9375 | 6.625 | 12.5 | 2.9375 | 6.625 | 14 | 3.6875 | 6.625 | 15 | 4.1875 | 6.625 | 15.5 | 4.4375 | 6.625 | 19 | 6.1875
8 | 8.625 | 13.5 | 2.4375 | 8.625 | 15 | 3.1875 | 8.625 | 15 | 3.1875 | 8.625 | 16.5 | 3.9375 | 8.625 | 18.5 | 4.9375 | 8.625 | 19 | 5.1875 | 8.625 | 21.75 | 6.5625
10 | 10.75 | 16 | 2.625 | 10.75 | 17.5 | 3.375 | 10.75 | 17.5 | 3.375 | 10.75 | 20 | 4.625 | 10.75 | 21.5 | 5.375 | 10.75 | 23 | 6.125 | 10.75 | 26.5 | 7.875
12 | 12.75 | 19 | 3.125 | 12.75 | 20.5 | 3.875 | 12.75 | 20.5 | 3.875 | 12.75 | 22 | 4.625 | 12.75 | 24 | 5.625 | 12.75 | 26.5 | 6.875 | 12.75 | 30 | 8.625
14 | 14 | 21 | 3.5 | 14 | 23 | 4.5 | 14 | 23 | 4.5 | 14 | 23.75 | 4.875 | 14 | 25.25 | 5.625 | 14 | 29.5 | 7.75 | 14
16 | 16 | 23.5 | 3.75 | 16 | 25.5 | 4.75 | 16 | 25.5 | 4.75 | 16 | 27 | 5.5 | 16 | 27.75 | 5.875 | 16 | 32.5 | 8.25 | 16
18 | 18 | 25 | 3.5 | 18 | 28 | 5 | 18 | 28 | 5 | 18 | 29.25 | 5.625 | 18 | 31 | 6.5 | 18 | 36 | 9 | 18
20 | 20 | 27.5 | 3.75 | 20 | 30.5 | 5.25 | 20 | 30.5 | 5.25 | 20 | 32 | 6 | 20 | 33.75 | 6.875 | 20 | 38.75 | 9.375 | 20
22 | 22 | 29.5 | 3.75 | 22 | 33 | 5.5 | 22 | 33 | 5.5 | 22 | 34.25 | 6.125 | 22 |  |  | 22 |  |  | 22
24 | 24 | 32 | 4 | 24 | 36 | 6 | 24 | 36 | 6 | 24 | 37 | 6.5 | 24 | 41 | 8.5 | 24 | 46 | 11 | 24
26 | 26 | 34.25 | 4.125 | 26 | 38.25 | 6.125 | 26 | 38.25 | 6.125 | 26 | 40 | 7 | 26 |  |  | 26 |  |  | 26
30 | 30 | 38.75 | 4.375 | 30 | 43 | 6.5 | 30 | 43 | 6.5 | 30 | 44.5 | 7.25 | 30 |  |  | 30 |  |  | 30
34 | 34 | 43.75 | 4.875 | 34 | 47.5 | 6.75 | 34 | 47.5 | 6.75 | 34 | 49 | 7.5 | 34 |  |  | 34 |  |  | 34
36 | 36 | 46 | 5 | 36 | 50 | 7 | 36 | 50 | 7 | 36 | 51.75 | 7.875 | 36 |  |  | 36 |  |  | 36
42 | 40 | 53 | 6.5 | 40 | 57 | 8.5 | 40 | 57 | 8.5 | 40 | 58.75 | 9.375 | 40 |  |  | 40 |  |  | 40
Green fields are for user entry
CASE A | Using the flange diameter for the larger line and the outdide diameter of the smallest line. |  |  |  | Large line Flange diameter = | [6 empty] | 0 |  | Inches
[5 empty] | Small line Pipe O. D. = | [6 empty] | 0 |  | Inches
[5 empty] | Minimum Clearance = | [6 empty] | 0 |  | Inches
[5 empty] | Insulation (if any) on the flange = | [6 empty] | 0 |  | Inches
[5 empty] | Insulation (if any) on small line = | [6 empty] | 0 |  | Inches
[5 empty] | Total line spacing (before round off) = | [6 empty] | 0 |  | Inches
CASE B | Using the flange diameter for the smaller, higher flange rating line and the outdide diameter of the larger line. |  |  |  | Smaller line (high pressure) Flange diameter = | [6 empty] | 0 |  | Inches
[5 empty] | Large line Pipe O. D. = | [6 empty] | 0 |  | Inches
[5 empty] | Minimum Clearance = | [6 empty] | 0 |  | Inches
[5 empty] | Insulation (if any) on the flange = | [6 empty] | 0 |  | Inches
[5 empty] | Insulation (if any) on small line = | [6 empty] | 0 |  | Inches
[5 empty] | Total line spacing (before round off) = | [6 empty] | 0 |  | Inches

## Metric
The purpose of this table is to provide a quick determination of the "worst case" distance a flange extends beyond the pipe O. D. for use during pipe line spacing |  |  |  |  | Quick Worst Case Flange Extension Chart (Metric) | [11 empty] | The Rule for line spacing is: Flange-to-pipe plus and inch. For the flange you should use the worst case.
All Ratings |  | 150# |  |  | 300# |  |  | 400# |  |  | 600# |  |  | 900# |  |  | 1500# |  |  | 2500#
Nominal Size (mm) | Actual Pipe O. D. (mm) | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm) |  | Flange O. D. (mm) | Flange Extension (mm)
76.2 | 88.9 | 191 | 51.05 | 88.9 | 210 | 60.55 | 88.9 | 210 | 60.55 | 88.9 | 210 | 60.55 | 88.9 | 241 | 76.05 | 88.9 | 267 | 89.05 | 88.9 | 305 | 108.05
101.6 | 114.3 | 229 | 57.35 | 114.3 | 254 | 69.85 | 114.3 | 254 | 69.85 | 114.3 | 273 | 79.35 | 114.3 | 292 | 88.85 | 114.3 | 311 | 98.35 | 114.3 | 356 | 120.85
152.4 | 168.28 | 279 | 55.36 | 168.28 | 318 | 74.86 | 168.28 | 318 | 74.86 | 168.28 | 356 | 93.86 | 168.28 | 381 | 106.36 | 168.28 | 394 | 112.86 | 168.28 | 483 | 157.36
203.2 | 219.08 | 343 | 61.96 | 219.08 | 381 | 80.96 | 219.08 | 381 | 80.96 | 219.08 | 419 | 99.96 | 219.08 | 470 | 125.46 | 219.08 | 483 | 131.96 | 219.08 | 552 | 166.46
254 | 273.05 | 406 | 66.475 | 273.05 | 445 | 85.975 | 273.05 | 445 | 85.975 | 273.05 | 508 | 117.475 | 273.05 | 546 | 136.475 | 273.05 | 584 | 155.475 | 273.05 | 673 | 199.975
304.8 | 323.85 | 483 | 79.575 | 323.85 | 521 | 98.575 | 323.85 | 521 | 98.575 | 323.85 | 559 | 117.575 | 323.85 | 610 | 143.075 | 323.85 | 673 | 174.575 | 323.85 | 762 | 219.075
355.6 | 355.6 | 533 | 88.7 | 355.6 | 584 | 114.2 | 355.6 | 584 | 114.2 | 355.6 | 603 | 123.7 | 355.6 | 641 | 142.7 | 355.6 | 749 | 196.7 | 355.6
406.4 | 406.4 | 597 | 95.3 | 406.4 | 648 | 120.8 | 406.4 | 648 | 120.8 | 406.4 | 686 | 139.8 | 406.4 | 705 | 149.3 | 406.4 | 826 | 209.8 | 406.4
457.2 | 457.2 | 635 | 88.9 | 457.2 | 711 | 126.9 | 457.2 | 711 | 126.9 | 457.2 | 743 | 142.9 | 457.2 | 787 | 164.9 | 457.2 | 914 | 228.4 | 457.2
508 | 508 | 699 | 95.5 | 508 | 775 | 133.5 | 508 | 775 | 133.5 | 508 | 813 | 152.5 | 508 | 857 | 174.5 | 508 | 984 | 238 | 508
609.6 | 609.6 | 813 | 101.7 | 609.6 | 914 | 152.2 | 609.6 | 914 | 152.2 | 609.6 | 940 | 165.2 | 609.6 | 1041 | 215.7 | 609.6 | 1168 | 279.2 | 609.6
Green fields for user entry
CASE A | Using the flange diameter for the larger line and the outside diameter of the smallest line. |  |  |  | Large line Flange diameter = | [6 empty] | 0 |  | millimeters
[5 empty] | Small line Pipe O. D. = | [6 empty] | 0 |  | millimeters
[5 empty] | Minimum Clearance = | [6 empty] | 0 |  | millimeters
[5 empty] | Insulation (if any) on the flange = | [6 empty] | 0 |  | millimeters
[5 empty] | Insulation (if any) on small line = | [6 empty] | 0 |  | millimeters
[5 empty] | Total line spacing (before round off) = | [6 empty] | 0 |  | millimeters
CASE B | Using the flange diameter for the smaller, higher flange rating line and the outside diameter of the larger line. |  |  |  | Small line (high pressure) Flg diameter = | [6 empty] | 0 |  | millimeters
[5 empty] | Large line Pipe O. D. = | [6 empty] | 0 |  | millimeters
[5 empty] | Minimum Clearance = | [6 empty] | 0 |  | millimeters
[5 empty] | Insulation (if any) on the flange = | [6 empty] | 0 |  | millimeters
[5 empty] | Insulation (if any) on small line = | [6 empty] | 0 |  | millimeters
[5 empty] | Total line spacing (before round off) = | [6 empty] | 0 |  | millimeters