## Summary
PIPING WEIGHT/ LOAD CALCULATION WORKBOOK
Purpose:
This Workbook provides a tool that is intended to provide a quick, easy and accurate method for the piping designer to use when calculating piping system weights. The workbook can be used to calculate the weight of the pipe, flanges, fittings, insulation and hydrotest water for a single size or for multi-size configurations.
Notes for use:
1 | At the bottom of the screen select (and click on) the tab for the size required for the line or system. Do the largest size first then the next size until finished with that line or system
2 | On the correct size sheet, enter quantities in the (Blue) quantity column. Lineal feet for Pipe and Insulation. Enter actual count for fittings, flanges and valves.
3 | For Hydrotest water add the lineal footage of the pipe plus add in a factor for the fittings and valves.
4 | At the bottom of each page there is a note "ADDITIONAL WEIGHT ITEM". This is the place to add in the weight of items such as Weld-O-Lets or any other previously unlisted items. For record purposes, define the item in the (Blue) space allowed. The data from this page and all other pages will be automatically posted to the summary table at the bottom of this page.
5 | For record purposes a project number, system or line description, originator and date may be entered at the top of each size sheet used. The same data may also be entered on this sheet.
6 | Do not try to enter data in any other spaces. This Workbook is password protected.
7 | For a piping load where the concentrated load is off center between two support points the higher individual load may be given. Example: where the center of the total calculated load is 85% closer to support point # 1 than #2 then input the decimal (.85) into the "Blue" box at the bottom of this page. The calculated load for Pipe Support #1 will be given.
8 | After all required data has been entered on a size page a copy should be ran for record purposes when required.
9 | When all weight work data for a system or individual line is complete and record copies have been run, close the file but do not "save" the changes. All previous data will be erased. You may then open the file again for another line or system.
Weight calculation summary section.
System or Line description |  |  |  | Data is entered here automaticly from individual size sheets.
Project - |  | Originator/Date -
Piping Weight Calculation from 2" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 3" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 4" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 6" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 8" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 10" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 12" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 14" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 16" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 18" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 20" NPS worksheet = |  |  |  | 0
Piping Weight Calculation from 24" NPS worksheet = |  |  |  | 0
|  |  |  | 0 | = TOTAL WEIGHT
Use this section only when calculating the weight distribution for unbalanced loads |  | PERCENT OF TOTAL IMPOSED AT SUP"T POINT |  | 0 | = RESULTANT LOAD (lbs) AT SUPPORT
|  | Example - | 0.85

## 2" NPS
|  |  | 2 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT | 3.65 |  | 0
PIPE | 80 / XS | 5.02
| 160 | 7.44
| XXS | 9.03 |  |  | 0
| 40 / STD WT | 1.46
HYDROTEST | 80 / XS | 1.28
WATER | 160 | 0.97
| XXS | 0.77 |  |  | 0
| 1" CAL SIL | 1.01
INSULATION | 1 1/2" CAL SIL | 1.69
| 2" CAL SIL | 2.5
| 2 1/2" CAL SIL | 3.38 |  |  | 0
| 40 / STD WT | 1.5
90 ELL | 80 / XS | 2.1
| 160 | 3
| XXS | 4 |  |  | 0
| 40 / STD WT | 0.9
45 ELL | 80 / XS | 1.1
| 160 | 1.6
| XXS | 2 |  |  | 0
| 40 / STD WT | 3
TEE | 80 / XS | 3.7
| 160 | 5
| XXS | 5.9 |  |  | 0
| 150# RF WN | 7
| 300# RF WN | 11
| 600# RF WN | 14
FLANGES | 150# RF SO | 6
| 300# RF SO | 9
| 600# RF SO | 11
| 150# RF BLIND | 5
| 300# RF BLIND | 10
| 600# RF BLIND | 12 |  |  | 0
| 150# GATE | 68
| 300# GATE | 75
| 600# GATE | 110
| 150# GLOBE | 53
VALVES | 300# GLOBE | 79
| 600# GLOBE | 115
| 150# CHECK | 45
| 300# CHECK | 62
| 600# CHECK | 100 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 3" NPS
|  |  | 3 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT | 7.58
PIPE | 80 / XS | 10.25
| 160 | 14.32
| XXS | 18.58 |  |  | 0
| 40 / STD WT | 3.2
HYDROTEST | 80 / XS | 2.86
WATER | 160 | 2.35
| XXS | 1.8 |  |  | 0
| 1 1/2" CAL SIL | 2.09
INSULATION | 2" CAL SIL | 2.98
| 2 1/2" CAL SIL | 3.98
| 3" CAL SIL | 5.11 |  |  | 0
| 40 / STD WT | 4.7
90 ELL | 80 / XS | 6.3
| 160 | 8.8
| XXS | 11.4 |  |  | 0
| 40 / STD WT | 2.5
45 ELL | 80 / XS | 3.3
| 160 | 4.5
| XXS | 5.7 |  |  | 0
| 40 / STD WT | 8.4
TEE | 80 / XS | 10
| 160 | 13.8
| XXS | 16.8 |  |  | 0
| 150# RF WN | 12
| 300# RF WN | 19
| 600# RF WN | 27
FLANGES | 150# RF SO | 9
| 300# RF SO | 17
| 600# RF SO | 20
| 150# RF BLIND | 10
| 300# RF BLIND | 20
| 600# RF BLIND | 24 |  |  | 0
| 150# GATE | 128
| 300# GATE | 145
| 600# GATE | 188
| 150# GLOBE | 80
VALVES | 300# GLOBE | 139
| 600# GLOBE | 191
| 150# CHECK | 65
| 300# CHECK | 120
| 600# CHECK | 152 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 4" NPS
|  |  | 4 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT | 10.79
PIPE | 80 / XS | 14.98
| 160 | 22.51
| XXS | 27.54 |  |  | 0
| 40 / STD WT | 5.51
HYDROTEST | 80 / XS | 4.98
WATER | 160 | 4.02
| XXS | 3.38 |  |  | 0
| 1" CAL SIL | 1.6
INSULATION | 1 1/2" CAL SIL | 2.49
| 2" CAL SIL | 3.49
| 3" CAL SIL | 6.03 |  |  | 0
| 40 / STD WT | 8.9
90 ELL | 80 / XS | 12.4
| 160 | 18.6
| XXS | 22.7 |  |  | 0
| 40 / STD WT | 4.5
45 ELL | 80 / XS | 6.2
| 160 | 9.3
| XXS | 11.4 |  |  | 0
| 40 / STD WT | 13.5
TEE | 80 / XS | 18.6
| 160 | 34.3
| XXS | 24.2 |  |  | 0
| 150# RF WN | 17
| 300# RF WN | 29
| 600# RF WN | 48
FLANGES | 150# RF SO | 15
| 300# RF SO | 26
| 600# RF SO | 43
| 150# RF BLIND | 19
| 300# RF BLIND | 31
| 600# RF BLIND | 47 |  |  | 0
| 150# GATE | 140
| 300# GATE | 215
| 600# GATE | 355
| 150# GLOBE | 140
VALVES | 300# GLOBE | 220
| 600# GLOBE | 320
| 150# CHECK | 100
| 300# CHECK | 185
| 600# CHECK | 280 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 6" NPS
|  |  | 6 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT | 18.97
PIPE | 80 / XS | 28.57
| 160 | 45.3
| XXS | 53.2 |  |  | 0
| 40 / STD WT | 12.51
HYDROTEST | 80 / XS | 11.29
WATER | 160 | 9.2
| XXS | 8.2 |  |  | 0
| 1 1/2" CAL SIL | 3.13
INSULATION | 2" CAL SIL | 4.54
| 3" CAL SIL | 7.42
| 4" CAL SIL | 11.2 |  |  | 0
| 40 / STD WT | 23.5
90 ELL | 80 / XS | 35.3
| 160 | 56
| XXS | 66 |  |  | 0
| 40 / STD WT | 11.8
45 ELL | 80 / XS | 17.7
| 160 | 28
| XXS | 33 |  |  | 0
| 40 / STD WT | 36.3
TEE | 80 / XS | 42.5
| 160 | 85
| XXS | 85 |  |  | 0
| 150# RF WN | 27
| 300# RF WN | 48
| 600# RF WN | 96
FLANGES | 150# RF SO | 22
| 300# RF SO | 45
| 600# RF SO | 95
| 150# RF BLIND | 29
| 300# RF BLIND | 56
| 600# RF BLIND | 101 |  |  | 0
| 150# GATE | 240
| 300# GATE | 420
| 600# GATE | 726
| 150# GLOBE | 250
VALVES | 300# GLOBE | 390
| 600# GLOBE | 782
| 150# CHECK | 200
| 300# CHECK | 330
| 600# CHECK | 550 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 8" NPS
|  |  | 8 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT. | 28.55
PIPE | 80 / XS | 43.4
| 160 | 74.7
| XXS | 72.4 |  |  | 0
| 40 | 21.69
HYDROTEST | 80 | 19.8
WATER | 160 | 15.8
| XXS | 16.1 |  |  | 0
| 1 1/2" CAL SIL | 4.06
INSULATION | 2" CAL SIL | 5.56
| 3" CAL SIL | 9.38
| 4" CALSIL | 13.3 |  |  | 0
| 40 | 46
90 ELL | 80 | 69
| 160 | 117
| XXS | 114 |  |  | 0
| 40 | 24
45 ELL | 80 | 36
| 160 | 61
| XXS | 60 |  |  | 0
| 40 | 61
TEE | 80 | 78
| 160 | 152
| XXS | 152 |  |  | 0
| 150# RF WN | 42
| 300# RF WN | 76
| 600# RF WN | 137
FLANGES | 150# RF SO | 33
| 300# RF SO | 67
| 600# RF SO | 135
| 150# RF BLIND | 48
| 300# RF BLIND | 90
| 600# RF BLIND | 159 |  |  | 0
| 150# GATE | 400
| 300# GATE | 700
| 600# GATE | 1220
| 150# GLOBE | 475
VALVES | 300# GLOBE | 850
| 600# GLOBE | 1300
| 150# CHECK | 390
| 300# CHECK | 620
| 600# CHECK | 910 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 10" NPS
|  |  | 10 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 40 / STD WT | 40.5
PIPE | 80 / XS | 54.7
| 160 | 115.7
0
| 40 / STD WT | 34.1
HYDROTEST | 80 / XS | 32.3
WATER | 160 | 24.6
0
| 1 1/2" CAL SIL | 5.1
INSULATION | 2" CAL SIL | 6.87
| 3" CAL SIL | 10.8
| 4" CAL SIL | 15.2 |  |  | 0
| 40 / STD WT | 84
90 ELL | 80 / XS | 112
| 160 | 238
0
| 40 / STD WT | 42.4
45 ELL | 80 / XS | 56
| 160 | 119
0
| 40 / STD WT | 104
TEE | 80 / XS | 132
| 160 | 280
0
| 150# RF WN | 60
| 300# RF WN | 110
| 600# RF WN | 225
FLANGES | 150# RF SO | 51
| 300# RF SO | 100
| 600# RF SO | 213
| 150# RF BLIND | 78
| 300# RF BLIND | 146
| 600# RF BLIND | 267 |  |  | 0
| 150# GATE | 630 |  | 0
| 300# GATE | 1050
| 600# GATE | 1880
| 150# GLOBE | 670
VALVES | 300# GLOBE | 1290
| 150# CHECK | 520
| 300# CHECK | 783
| 600# CHECK | 1440 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 12" NPS
|  |  | 12 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| STD WT | 49.6
PIPE | XS | 65.4
| 160 | 160.3
0
| STD WT | 49
HYDROTEST | XS | 47
WATER | 160 | 34
0
| 1 1/2" CAL SIL | 5.19
INSULATION | 2" CAL SIL | 7.92
| 3" CAL SIL | 12.3
| 4" CAL SIL | 17.2 |  |  | 0
| STD WT | 123
90 ELL | XS | 162
| 160 | 397
0
| STD WT | 62
45 ELL | XS | 81
| 160 | 199
0
| STD WT | 162
TEE | XS | 187
| 160 | 429
0
| 150# RF WN | 88
| 300# RF WN | 163
| 600# RF WN | 272
FLANGES | 150# RF SO | 72
| 300# RF SO | 140
| 600# RF SO | 261
| 150# RF BLIND | 118
| 300# RF BLIND | 209
| 600# RF BLIND | 341 |  |  | 0
| 150# GATE | 830
| 300# GATE | 1490
| 600# GATE | 2630
VALVES
| 150# CHECK | 775
| 300# CHECK | 1300
| 600# CHECK | 1970 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 14" NPS
|  |  | 14 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| STD WT | 54.6
PIPE | XS | 72.1
| 160 | 189.1
0
| STD WT | 59.7
HYDROTEST | XS | 57.5
WATER | 160 | 42.6
0
| 1 1/2" CAL SIL | 5.9
INSULATION | 2" CAL SIL | 8.3
| 3" CAL SIL | 12.6
| 4" CAL SIL | 15.1 |  |  | 0
| STD WT | 158
90 ELL | XS | 208
| 160 | 546
0
| STD WT | 80
45 ELL | XS | 104
| 160 | 273
0
| STD WT | 226
TEE | XS | 280
0
| 150# RF WN | 130
| 300# RF WN | 217
| 600# RF WN | 406
FLANGES | 150# RF SO | 96
| 300# RF SO | 195
| 600# RF SO | 318
| 150# RF BLIND | 142
| 300# RF BLIND | 267
| 600# RF BLIND | 437 |  |  | 0
| 150# GATE | 1150
| 300# GATE | 2170
| 600# GATE | 3455
VALVES
| 150# CHECK | 1213
| 300# CHECK | 1764
| 600# CHECK | 2640 |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 16" NPS
|  |  | 16 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| 30/STD WT | 62.6
PIPE | 40/ XS | 82.8
| 80 | 136.5
0
| 30/STD WT | 79.1
HYDROTEST | 40/XS | 76.5
WATER | 80 | 69.7
0
| 1 1/2" CAL SIL | 6.65
INSULATION | 2" CAL SIL | 9.02
| 3" CAL SIL | 14.1
| 4" CAL SIL | 19.7 |  |  | 0
| 30/STD WT | 208
90 ELL | 40/XS | 273
0
| STD WT | 104
45 ELL | XS | 137
0
| STD WT | 250
TEE | XS | 369
0
| 150# RF WN | 142
| 300# RF WN | 288
| 600# RF WN | 577
FLANGES | 150# RF SO | 108
| 300# RF SO | 262
| 600# RF SO | 442
| 150# RF BLIND | 185
| 300# RF BLIND | 349
| 600# RF BLIND | 603 |  |  | 0
| 150# GATE | 1580
| 300# GATE | 2800
| 600# GATE | 4375
VALVES
150# CHECK
| 300# CHECK | 1225
| 600# CHECK |  |  |  | 0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 18"NPS
|  |  | 18 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| STD WT | 70.6
PIPE | XS | 93.5
0
| STD WT | 101.2
HYDROTEST | XS | 98.4
WATER
0
| 1 1/2" CAL SIL | 7.4
INSULATION | 2" CAL SIL | 10
| 3" CAL SIL | 15.6
| 4" CAL SIL | 21.7 |  |  | 0
| STD WT | 263
90 ELL | XS | 347
0
| STD WT | 132
45 ELL | XS | 174
0
| STD WT | 333
TEE | XS | 425
0
| 150# RF WN | 160
| 300# RF WN | 355
| 600# RF WN | 652
FLANGES | 150# RF SO | 140
| 300# RF SO | 331
| 600# RF SO | 573
| 150# RF BLIND | 229
| 300# RF BLIND | 440
| 600# RF BLIND | 762 |  |  | 0
| 150# GATE | 1898
| 300# GATE | 3319
| 600# GATE | 6020
VALVES
0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 20"NPS
|  |  | 20 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| STD WT | 78.6
PIPE | XS | 104.1
0
| STD WT | 126
HYDROTEST | XS | 122.8
WATER
0
| 1 1/2" CAL SIL | 8.15
INSULATION | 2" CAL SIL | 11
| 3" CAL SIL | 17.1
| 4" CAL SIL | 23.6 |  |  | 0
| STD WT | 323
90 ELL | XS | 438
0
| STD WT | 162
45 ELL | XS | 228
0
| STD WT | 504
TEE | XS | 583
0
| 150# RF WN | 196
| 300# RF WN | 431
| 600# RF WN | 811
FLANGES | 150# RF SO | 181
| 300# RF SO | 378
| 600# RF SO | 733
| 150# RF BLIND | 298
| 300# RF BLIND | 545
| 600# RF BLIND | 976 |  |  | 0
| 150# GATE | 2228
| 300# GATE | 4278
| 600# GATE | 7015
VALVES
0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0

## 24" NPS
|  |  | 24 " NPS |  | PROJECT:
PIPING WEIGHT CALCULATION WORKSHEET
DESCRIPTION : |  |  |  |  | ORIGINATOR / DATE
| SCHEDULE, | WEIGHT (lbs) |  | SUB TOTAL
ITEM | TYPE | PER FOOT | QUANTITY | PER LINE ITEM | TOTAL BY
| OR CLASS | OR PER EACH |  |  | CATEGORY
| STD WT | 94.6
PIPE | XS | 125.5
0
| STD WT | 183.8
HYDROTEST | XS | 180.1
WATER
0
| 1 1/2" CAL SIL | 9.65
INSULATION | 2" CAL SIL | 13
| 3" CAL SIL | 20
| 4" CAL SIL | 27.5 |  |  | 0
| STD WT | 500
90 ELL | XS | 622
0
| STD WT | 252
45 ELL | XS | 311
0
| STD WT | 765
TEE | XS | 934
0
| 150# RF WN | 295
| 300# RF WN | 632
| 600# RF WN | 1157
FLANGES | 150# RF SO | 245
| 300# RF SO | 577
| 600# RF SO | 1056
| 150# RF BLIND | 446
| 300# RF BLIND | 841
| 600# RF BLIND | 1355 |  |  | 0
| 150# GATE | 3350
| 300# GATE | 7529
| 600# GATE | 9360
VALVES
0
ADDITIONAL WEIGHT ITEM ( DEFINE ) =
|  |  |  | TOTAL WEIGHT THIS SHEET | 0