## Sheet1
Nominal Pipe Size | Schedule (Wall Thickness) | Corrosion Allowance | Pipe + Vapour Insulation | [5 empty] | Pipe + Liquid + Insulation | [5 empty] | Bare Pipe |  | Bare Pipe |  | Nominal Pipe Size
[15 empty] | (Empty) |  | (Water Filled)
|  |  | Up To 175°C |  | 176 To 315°C |  | 316 To 400°C |  | Up To 175°C |  | 176 To 315°C |  | 316 To 400°C |  | Up To 175°C |  | Up To 175°C
|  |  | Span | Weight | Span | Weight | Span | Weight | Span | Weight | Span | Weight | Span | Weight | Span | Weight | Span | Weight
|  |  | M | KG/M | M | KG/M | M | KG/M | M | KG/M | M | KG/M | M | KG/M | M | KG/M | M | KG/M
3/4" | 40 | 1.27 | 3.5 | 2.60 | 3.5 | 3.72 | * 2.5 | 6.44 | 3.5 | 2.95 | * 3.0 | 4.06 | * 2.0 | 6.79 | 4.0 | 1.69 | 3.4 | 2.04 | 3/4"
1" | 40 | 1.27 | 4.0 | 3.53 | 4.0 | 4.81 | * 3.0 | 7.62 | 4.0 | 4.08 | 3.5 | 5.36 | * 2.5 | 8.17 | 5.0 | 2.50 | 4.0 | 3.06 | 1"
1 1/2" | 40 | 1.27 | 5.5 | 5.33 | 5.0 | 6.71 | * 4.0 | 10.07 | 5.0 | 6.64 | 4.5 | 8.02 | * 3.5 | 11.38 | 6.0 | 4.05 | 5.0 | 5.37 | 1 1/2"
2" | 40 | 2.54 | 5.5 | 7.29 | 5.5 | 10.06 | * 3.5 | 15.05 | 5.0 | 9.45 | 4.5 | 12.07 | * 3.0 | 17.20 | 6.5 | 5.44 | 5.5 | 7.60 | 2"
2 1/2" | 40 | 2.54 | 7.0 | 10.74 | 6.0 | 13.77 | * 5.0 | 17.90 | 6.0 | 13.83 | 5.5 | 16.85 | * 4.5 | 20.98 | 7.5 | 8.63 | 6.0 | 11.72 | 2 1/2"
3" | 40 | 2.54 | 8.0 | 13.74 | 6.5 | 17.04 | * 5.5 | 23.11 | 6.5 | 18.50 | 6.0 | 21.86 | * 5.0 | 27.87 | 8.0 | 11.29 | 6.5 | 16.06 | 3"
4" | 40 | 2.54 | 8.0 | 19.39 | 7.5 | 22.92 | 7.0 | 30.55 | 7.0 | 27.58 | 7.0 | 31.12 | * 5.5 | 38.77 | 9.0 | 16.07 | 7.0 | 24.28 | 4"
6" | 40 | 2.54 | 10 | 32.87 | 9.5 | 40.25 | 8.5 | 47.77 | 9.0 | 51.22 | 8.0 | 58.60 | * 7.5 | 66.4 | 10.0 | 28.26 | 8.5 | 46.91 | 6"
8" | 40 | 2.54 | 11.5 | 49.04 | 11.0 | 57.09 | 10.0 | 66.52 | 10.0 | 81.18 | 10.0 | 89.23 | * 9.0 | 98.78 | 12.0 | 42.55 | 10.0 | 74.83 | 8"
10" | 40 | 2.54 | 13.5 | 68.11 | 13.0 | 77.68 | 12.0 | 90.48 | 11.0 | 118.87 | 10.5 | 128.44 | * 10.0 | 141.32 | 14.0 | 60.31 | 11.5 | 111.20 | 10"
12" | STD | 2.54 | 14.5 | 85.02 | 14.0 | 93.90 | 13.0 | 107.98 | 11.5 | 157.98 | 11.5 | 166.87 | * 11.0 | 180.95 | 15.0 | 73.88 | 12.0 | 146.87 | 12"
14" | STD | 2.54 | 15.0 | 93.93 | 14.5 | 102.68 | 13.5 | 119.05 | 12.0 | 182.78 | 12.0 | 192.30 | * 11.5 | 207.97 | 16.0 | 81.33 | 12.5 | 170.28 | 14"
16" | STD | 2.54 | 16.0 | 107.45 | 15.0 | 117.12 | 14.0 | 136.17 | 13.0 | 225.01 | 12.5 | 234.86 | * 11.5 | 253.91 | 17.0 | 93.27 | + 13.0 | 211.11 | 16"
18" | STD | 2.54 | 17.0 | 120.84 | 16.5 | 132.45 | 15.0 | 152.83 | 13.5 | 271.44 | 13.0 | 283.05 | * 12.0 | 302.87 | 18.0 | 105.16 | + 13.5 | 255.80 | 18"
20" | STD | 2.54 | 18.0 | 134.23 | 17.0 | 146.14 | 16.0 | 169.65 | 14.0 | 321.74 | 13.5 | 333.16 | * 12.5 | 356.67 | 19.0 | 117.15 | + 14.0 | 304.91 | 20"
24" | STD | 2.54 | 20.0 | 161.02 | 19.0 | 175.31 | 17.5 | 202.84 | 14.5 | 434.54 | 14.0 | 449.57 | * 13.0 | 476.58 | + 20.5 | 141.12 | + 15.0 | 415.39 | 24"
3/4" | 80 | 2.54 | 3.5 | 3.11 | 3.0 | 4.18 | * 2.0 | 6.95 | 3.0 | 3.39 | 3.0 | 4.51 | * 1.5 | 7.23 | 4.0 | 2.20 | 3.5 | 2.48 | 3/4"
1" | 80 | 2.54 | 4.0 | 4.26 | 3.5 | 5.54 | * 3.0 | 8.35 | 4.0 | 4.72 | 3.5 | 6.16 | * 2.5 | 8.90 | 5.0 | 3.24 | 4.0 | 3.70 | 1"
1 1/2" | 80 | 2.54 | 5.0 | 6.68 | 4.5 | 8.07 | * 4.0 | 11.43 | 5.0 | 7.83 | 4.5 | 9.21 | * 4.0 | 12.57 | 6.0 | 5.41 | 5.0 | 6.55 | 1 1/2"
2" | 80 | 2.54 | 6.0 | 9.33 | 5.0 | 12.10 | * 4.0 | 17.08 | 5.5 | 11.24 | 5.0 | 14.00 | * 4.0 | 18.99 | 6.5 | 7.48 | 6.0 | 9.40 | 2"
2 1/2" | 80 | 2.54 | 7.0 | 13.53 | 6.0 | 16.55 | 5.5 | 20.54 | 6.0 | 16.25 | 6.0 | 19.27 | * 5.0 | 23.41 | 7.0 | 11.41 | 6.5 | 14.14 | 2 1/2"
3" | 80 | 2.54 | 7.5 | 17.72 | 7.0 | 21.09 | 6.0 | 27.17 | 7.0 | 21.98 | 6.5 | 25.34 | 6.0 | 31.43 | 7.5 | 15.27 | 7.0 | 19.50 | 3"
4" | 80 | 2.54 | 8.0 | 25.61 | 7.5 | 29.15 | 7.0 | 36.28 | 7.5 | 33.02 | 7.0 | 36.56 | 6.5 | 43.69 | 8.5 | 22.32 | 8.0 | 27.74 | 4"
6" | 80 | 2.54 | 10.0 | 47.20 | 9.5 | 54.57 | 9.0 | 61.31 | 9.5 | 64.00 | 9.0 | 71.37 | 8.5 | 78.86 | 10.5 | 42.56 | 9.5 | 59.38 | 6"
8" | 80 | 2.54 | 12.0 | 71.13 | 11.0 | 79.20 | 10.5 | 88.55 | 10.5 | 100.59 | 10.0 | 108.65 | 10.0 | 118.00 | 12.0 | 64.64 | 11.0 | 94.11 | 8"
10" | XS | 2.54 | 13.0 | 89.42 | 12.5 | 98.96 | 12.0 | 111.76 | 11.5 | 137.57 | 11.0 | 147.11 | 10.5 | 159.90 | 13.5 | 81.55 | 12.0 | 129.74 | 10"
12" | XS | 2.54 | 14.0 | 108.56 | 13.5 | 117.31 | 13.0 | 132.03 | 12.5 | 178.52 | 12.0 | 187.33 | 11.5 | 201.54 | 15.0 | 97.46 | 13.0 | 167.44 | 12"
14" | XS | 2.54 | 15.0 | 119.38 | 14.5 | 128.73 | 14.0 | 145.10 | 13.0 | 205.00 | 12.5 | 214.36 | 12.0 | 230.72 | 15.5 | 107.39 | 13.5 | 193.02 | 14"
16" | XS | 2.54 | 16.0 | 136.85 | 15.5 | 147.18 | 15.0 | 166.23 | 13.5 | 250.82 | 13.0 | 261.14 | 13.0 | 280.19 | 16.5 | 123.30 | + 14.0 | 237.31 | 16"
18" | XS | 2.54 | 17.0 | 154.32 | 16.5 | 165.93 | 16.0 | 187.21 | 14.0 | 300.77 | 14.0 | 312.38 | 13.5 | 333.36 | 18.0 | 139.15 | + 14.5 | 285.45 | 18"
20" | XS | 2.54 | 18.0 | 173.07 | 17.0 | 185.43 | 17.0 | 208.94 | 15.0 | 355.92 | 14.5 | 368.28 | 14.0 | 391.79 | 19.0 | 155.12 | + 15.0 | 338.04 | 20"
24" | XS | 2.54 | 20.0 | 206.56 | 19.0 | 221.14 | 18.0 | 248.67 | 16.0 | 474.62 | 15.0 | 489.20 | 15.0 | 517.18 | + 20.5 | 187.06 | + 15.5 | 455.58 | 24"
1" | XXS | 6.35 | 4.0 | 6.62 | 4.0 | 7.75 | * 3.0 | 10.57 | 4.0 | 6.80 | 3.5 | 7.93 | * 3.0 | 10.83 | 4.5 | 5.45 | 4.0 | 5.63 | 1"
1 1/2" | XXS | 6.35 | 5.0 | 10.82 | 4.5 | 12.20 | 4.0 | 15.57 | 5.0 | 11.42 | 4.5 | 12.81 | 4.0 | 16.18 | 5.5 | 9.56 | 5.0 | 10.18 | 1 1/2"
2" | XXS | 6.35 | 6.0 | 15.30 | 5.5 | 18.07 | 4.5 | 23.04 | 5.5 | 16.44 | 5.0 | 19.21 | 4.5 | 24.18 | 6.5 | 13.44 | 6.0 | 14.60 | 2"
2 1/2" | 160 | 6.35 | 6.5 | 17.02 | 6.0 | 19.69 | 5.0 | 24.15 | 6.0 | 19.32 | 5.5 | 22.34 | 5.0 | 26.44 | 7.0 | 14.92 | 6.5 | 17.21 | 2 1/2"
3" | 160 | 6.35 | 7.0 | 23.75 | 6.5 | 27.11 | 6.0 | 33.13 | 7.0 | 27.25 | 6.5 | 30.61 | 6.0 | 36.62 | 7.5 | 21.35 | 7.0 | 24.84 | 3"
4" | 120 | 6.35 | 8.0 | 31.53 | 7.5 | 35.08 | 7.0 | 45.09 | 7.5 | 38.19 | 7.0 | 41.73 | 7.0 | 50.85 | 8.5 | 28.32 | 8.0 | 34.97 | 4"
6" | 80 | 6.35 | 10.0 | 47.20 | 9.5 | 54.57 | 8.5 | 61.31 | 8.5 | 64.00 | 8.0 | 71.37 | 8.0 | 78.86 | 10.5 | 42.56 | 9.0 | 59.38 | 6"
8" | 80 | 6.35 | 11.5 | 71.13 | 11.0 | 79.20 | 10.0 | 88.55 | 10.0 | 100.59 | 9.5 | 108.65 | 9.0 | 118.00 | 12.0 | 64.64 | 10.0 | 94.11 | 8"
10" | XS | 6.35 | 13.0 | 89.42 | 12.5 | 98.96 | 11.5 | 111.76 | 11.0 | 137.57 | 10.5 | 147.11 | 10.0 | 159.90 | 13.5 | 81.55 | 11.0 | 129.74 | 10"
12" | XS | 6.35 | 14.0 | 108.56 | 13.5 | 117.31 | 12.5 | 132.03 | 11.5 | 178.52 | 11.0 | 187.33 | 10.5 | 201.54 | 15.0 | 97.46 | 11.5 | 167.44 | 12"
14" | XS | 6.35 | 15.0 | 119.38 | 14.0 | 128.73 | 13.5 | 145.10 | 12.0 | 205.00 | 11.5 | 214.36 | 11.0 | 230.72 | 16.0 | 107.39 | 12.0 | 193.02 | 14"
16" | XS | 6.35 | 16.0 | 136.85 | 15.0 | 147.18 | 14.5 | 166.23 | 12.5 | 250.82 | 12.0 | 261.14 | 11.5 | 280.19 | 17.0 | 123.30 | + 12.5 | 237.31 | 16"
18" | XS | 6.35 | 17.0 | 154.32 | 16.0 | 165.93 | 15.0 | 187.21 | 13.0 | 300.77 | 12.5 | 312.38 | 12.0 | 333.36 | 18.0 | 139.15 | + 13.0 | 285.45 | 18"
20" | XS | 6.35 | 18.0 | 173.07 | 17.0 | 185.43 | 16.0 | 208.94 | 13.5 | 355.92 | 13.5 | 368.28 | 13.0 | 391.79 | 19.0 | 155.12 | + 14.0 | 338.04 | 20"
24" | XS | 6.35 | 19.5 | 206.56 | 18.0 | 221.14 | 17.5 | 248.67 | 14.0 | 474.02 | 14.0 | 489.20 | 14.0 | 517.18 | + 20.5 | 187.06 | + 14.5 | 455.58 | 24"
Notes
1. | * Spans limited by stress (all others limited by deflection). | [8 empty] | 5. | Pulsating lines: Spans indicated above shall not be used.
2. | + Pipe walls require reinforcing at point of support. | [8 empty] | 6. | Tempratures in the above table are in degrees Celsius,
as indicated (maximum 400 °C)
3. | Allowable spans are based on a maximum bending stress
| of 41.37 Mpa (6000 PSI) or a maximum deflection | [8 empty] | 7. | Corrosion Allowance: As indicated, spans can be used
| of 12.7 MM (0.5in) | [9 empty] | for lines of equivalent or smaller allowance than those
specified in the above table.
4. | Hydrostatic testing: Spans are adequate without the
| addition of auxiliary supports for insulated lines and | [8 empty] | 8. | All dimensions are in millimeters, except as noted.
lines on shoes.